## Reminders - updated (hidden)
The following are some general notes and reminders last updated 2021-03-05
Scoring and Certification Levels (Note that this is subject to change and may vary - always check the version of the rating system you're using
Projects must achieve all preconditions as well as a certain number of points to earn different levels of certification:
| Total points achieved | WELL Certification |  | WELL Core Certification
|  | Minimum points per concept | Level of certification | Minimum points per concept | Level of certification
| 40 pts | 0 | WELL Bronze | 0 | WELL Core Bronze
| 50 pts | 1 | WELL Silver | 0 | WELL Core Silver
| 60 pts | 2 | WELL Gold | 0 | WELL Core Gold
| 80 pts | 3 | WELL Platinum | 0 | WELL Core Platinum
No more than 100 points total across the ten concepts. Projects can also pursue an additional ten points for Innovation.
At the point of submitting for Documentation Review, projects must submit a scorecard that contains a selection of
points and Features in accordance with these rules.
Project Version (Created 2021-03-05)
Template functionality
Manually adjust points in column G of the Review comments tab, as needed to account for Feature level point caps
If a change is made, highlight the cell red for visibility during QC
If additional space is needed in a Review Comment cell, insert a row underneath the current row the cell is in, then merge each cell in that row with the new cell directly underneath it

## Overview
2202025160 - Pohlad Office - Gateway22
|  | The WELL Building Standard v2.0 (Q1 2021) |  |  |  |  | 44 | Achieved
|  | 2022-11-15 | [8 empty] | Last updated 2021-03-05
|  | Preliminary Performance Review |  |  |  |  | 16 | Pending Documentation |  |  | Review phase drives additional options. Ensure to fill this out correctly.
[7 empty] | 0 | Pending Documentation & On-Site
[7 empty] | 0 | Anticipated, Pending On-Site
[7 empty] | 0 | Not Achieved
|  |  |  | Preconditions Pending Documentation: 12 | 60 | 0 | 60 | Total Points Attempted
Type | Concept | Type | Feature | Part | Scorecard Points | Pursuing | Attempted | Status | Achieved | Not Achieved or Pending |  | Not Ant/Not Ach | On-Site | Pending Doc | Pending doc/On-site | Anticipated/achieved | Precondition pending | Preconditions Pend On-Site Only
P | AIR | P | A01. Air Quality | A01.1 Meet Thresholds for Particulate Matter | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | A01.2 Meet Thresholds for Organic Gases | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | A01.3 Meet Thresholds for Inorganic Gases | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | A01.4 Meet Radon Threshold | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | A01.5 Monitor Air Parameters | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | A02. Smoke-Free Environment | A02.1 Prohibit Indoor Smoking | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | A02.2 Prohibit Outdoor Smoking | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | A03. Ventilation Design | A03.1 Ensure Adequate Ventilation | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | A04. Construction Pollution Management | A04.1 Mitigate Construction Pollution | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | A05. Enhanced Air Quality | A05.1 Meet Enhanced Thresholds for Particulate Matter | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | A05.2 Meet Enhanced Thresholds for Organic Gases | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | A05.3 Meet Enhanced Thresholds for Inorganic Gases | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  | O | A06. Enhanced Ventilation Design | A06.1 Increase Outdoor Air Supply | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | A06.2 Implement Demand-Controlled Ventilation | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A07. Operable Windows | A07.1 Provide Operable Windows | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | A07.2 Manage Window Use | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A08. Air Quality Monitoring and Awareness | A08.1 Install Indoor Air Monitors | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | A08.2 Promote Air Quality Awareness | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A09. Pollution Infiltration Management | A09.1 Design Healthy Entryways | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | A09.2 Perform Envelope Commissioning | 0 | No |  | Withdrawn |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A10. Combustion Minimization | A10.1 Manage Combustion | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A11. Source Separation | A11.1 Manage Pollution and Exhaust | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A12. Air Filtration | A12.1 Implement Particle Filtration | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | A13. Enhanced Supply Air | A13.1 Improve Air Supply | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | A14. Microbe and Mold Control | A14.1 Implement Ultraviolet Air Treatment | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  |  | 5 |  | 5 |  | 2 | 3 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | WATER | P | W01. Water Quality Indicators | W01.1 Verify Water Quality Indicators | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  | P | W02. Drinking Water Quality | W02.1 Meet Chemical Thresholds | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | W02.2 Meet Thresholds for Organics and Pesticides | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | W03.Basic Water Management | W03.1 Monitor Chemical and Biological Water Quality | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | W03.2 Implement Legionella Management Plan | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | W04. Enhanced Water Quality | W04.1 Meet Thresholds for Drinking Water Taste | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  | O | W05. Drinking Water Quality Management | W05.1 Assess and Maintain Drinking Water Quality | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | W05.2 Promote Drinking Water Transparency | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | W06. Drinking Water Promotion | W06.1 Ensure Drinking Water Access | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | W07. Moisture Management | W07.1 Design Envelope for Moisture Protection | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | W07.2 Design Interiors for Moisture Management | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | W07.3 Implement Mold and Moisture Management Plan | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | W08. Hygiene Support | W08.1 Provide Bathroom and Handwashing Accommodations | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | W08.2 Enhance Bathroom Accommodations | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | W08.3 Support Effective Handwashing | 1 | Yes | 1 | Pending Documentation |  | 1 | W09 Hidden | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | W08.4 Provide Handwashing Supplies And Signage | 0 | No |  | Not Attempted |  |  | W09 Hidden | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | W09. β - Onsite Non-Potable Water Reuse | W09.1 Implement Safety Plan for Non-Potable Water Capture and Reuse | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 3 |  | 3 |  | 1 | 2 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | NOURISHMENT | P | N01. Fruits and Vegetables | N01.1 Provide Fruit and Vegetables | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | N01.2 Promote Fruit and Vegetable Visibility | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  | P | N02. Nutritional Transparency | N02.1 Provide Nutritional Information | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | N02.2 Address Food Allergens | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | N02.3 Label Sugar Content | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | N03. Refined Ingredients | N03.1 Limit Total Sugars | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | N03.2 Promote Whole Grains | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N04. Food Advertising | N04.1 Optimize Food Advertising | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N05. Artificial Ingredients | N05.1 Limit Artificial Ingredients | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N06. Portion Sizes | N06.1 Promote Healthy Portions | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N07. Nutrition Education | N07.1 Provide Nutrition Education | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N08. Mindful Eating | N08.1 Support Mindful Eating | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  | O | N09. Special Diets | N09.1 Accommodate Special Diets | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | N09.2 Label Food Allergens | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N10. Food Preparation | N10.1 Provide Meal Support | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  | O | N11. Responsible Food Sourcing | N11.1 Implement Responsible Sourcing | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N12. Food Production | N12.1 Provide Gardening Space | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | N13. Local Food Environment | N13.1 Ensure Local Food Access | 1 | Yes | 1 | Achieved | 1 |  | N14 Hidden | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | N14. β - Red and Processed Meats | N14.1 Limit Red and Processed Meats | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 4 |  | 4 |  | 3 | 1 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | LIGHT | P | L01. Light Exposure | L01.1 Provide Indoor Light | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | L02. Visual Lighting Design | L02.1 Light Levels for Visual Acuity | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
O |  | O | L03. Circadian Lighting Design | L03.1 Meet Lighting for Day-Active People | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | L04. Electric Light Glare Control | L04.1 Manage Glare from Electric Lighting | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | L05. Daylight Design Strategies | L05.1 Implement Daylight Plan | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | L05.2 Integrate Solar Shading | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  | O | L06. Daylight Simulation | L06.1 Conduct Daylight Simulation | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | L07. Visual Balance | L07.1 Balance Visual Lighting | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | L08. Electric Light Quality | L08.1 Enhance Color Rendering Quality | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | L08.2 Manage Flicker | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  | O | L09. Occupant Lighting Control | L09.1 Enhance Occupant Controllability | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | L09.2 Provide Supplemental Lighting | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 4 |  | 4 |  | 3 | 1 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | MOVEMENT | P | V01. Active Buildings and Communities | V01.1 Design Active Buildings and Communities | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | V02. Ergonomic Workstation Design | V02.1 Support Visual Ergonomics | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | V02.2 Provide Height-Adjustable Work Surfaces | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | V02.3 Provide Chair Adjustability | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | V02.4 Provide Support at Standing Workstations | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | V02.5 Provide Workstation Orientation | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | V03. Circulation Network | V03.1 Design Aesthetic Circulation Staircases | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | V03.2 Integrate Point-of-Decision Signage | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | V03.3 Promote Visible Stairs | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | V04. Facilities for Active Occupants | V04.1 Provide Cycling Infrastructure | 2 | Yes | 2 | Pending Documentation |  | 2 |  | FALSE | FALSE | 2 | FALSE | FALSE | 0 | 0
O |  |  |  | V04.2 Provide Showers, Lockers and Changing Facilities | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | V05. Site Planning and Selection | V05.1 Select Sites with Pedestrian-friendly Streets | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | V05.2 Select Sites with Access to Mass Transit | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  | O | V06. Physical Activity Opportunities | V06.1 Offer Physical Activity Opportunities | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | V07. Active Furnishings | V07.1 Provide Active Workstations | 2 | Yes | 2 | Pending Documentation |  | 2 |  | FALSE | FALSE | 2 | FALSE | FALSE | 0 | 0
O |  | O | V08. Physical Activity Spaces and Equipment | V08.1 Provide Indoor Activity Spaces | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | V08.2 Provide Outdoor Physical Activity Space | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | V09. Physical Activity Promotion | V09.1 Offer Physical Activity Incentives | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | V10. Self-Monitoring | V10.1 Provide Self-Monitoring Tools | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | V11. β Ergonomics Programming | V11.1 Implement an Ergonomics Program | 0 | 0 |  |  |  |  | V11 Hidden | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | V11.2 Commit to Ergonomic Improvements | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | V11.3 Support Remote Work Ergonomics | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 11 |  | 11 |  | 6 | 5 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | THERMAL COMFORT | P | T01. Thermal Performance | T01.1 Provide Acceptable Thermal Environment | 0 | Required | Required | Pending Documentation | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
P |  |  |  | T01.2 Monitor Thermal Parameters | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | T02. Verified Thermal Performance | T02.1 Survey for Thermal Comfort | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T03. Thermal Zoning | T03.1 Ensure Thermostat Control | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T04. Individual Thermal Control | T04.1 Provide Personal Cooling Options | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | T04.2 Provide Personal Heating Options | 1 | Yes | 1 | Pending Documentation |  | 1 |  | FALSE | FALSE | 1 | FALSE | FALSE | 0 | 0
O |  |  |  | T04.3 Allow Flexible Dress Code | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | T05. Radiant Thermal Comfort | T05.1 Implement Radiant Heating | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | T05.2 Implement Radiant Cooling | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T06. Thermal Comfort Monitoring | T06.1 Monitor Thermal Environment | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T07. Humidity Control | T07.1 Manage Relative Humidity | 0 | No |  | Not Attempted |  |  | T08/T09 Hidden | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T08. β - Enhanced Operable Windows | T08.1 Provide Windows with Multiple Opening Modes | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | T09. β - Humidity Control | T09.1 Manage Outdoor Heat | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | T09.2 Avoid Excessive Wind | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | T09.3 Support Outdoor Nature Access | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 3 |  | 3 |  | 1 | 2 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | SOUND | P | S01. Sound Mapping | S01.1 Label Acoustic Zones | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | S01.2 Provide Acoustic Design Plan | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | S02. Maximum Noise Levels | S02.1 Limit Background Noise Levels | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | S03. Sound Barriers | S03.1 Design for Sound Isolation at Walls and Doors | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | S03.2 Achieve Sound Isolation at Walls | 2 | Yes | 2 | Pending Documentation |  | 2 |  | FALSE | FALSE | 2 | FALSE | FALSE | 0 | 0
O |  | O | S04. Reverberation Time | S04.1 Achieve Reverberation Time Thresholds | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | S05. Sound Reducing Surfaces | S05.1 Implement Sound Reducing Surfaces | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | S06. Minimum Background Sound | S06.1 Provide Minimum Background Sound | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | S06.2 Provide Enhanced Speech Reduction | 0 | No |  | Not Attempted |  |  | S07/S08 Hidden | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | S07. β - Impact Noise Management | S07.1 Specify Impact Noise Reducing Flooring | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | S07.2 Meet Thresholds for Impact Noise Rating | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | S08. β - Enhanced Audio Devices | S08.1 Provide Enhanced Speech Intelligibility | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | S08.2 Prioritize Audio Devices and Policies | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 3 |  | 3 |  | 1 | 2 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | MATERIALS | P | X01. Material Restrictions | X01.1 Restrict Asbestos | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | X01.2 Restrict Mercury | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | X01.3 Restrict Lead | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | X02. Interior Hazardous Material Management | X02.1 Manage Asbestos Hazards | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | X02.2 Manage Lead Paint Hazards | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | X02.3 Manage Polychlorinated Biphenyl (PCB) Hazards | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | X03. CCA and Lead Management | X03.1 Manage Exterior CCA Hazards | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | X03.2 Manage Lead Hazards | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | X04. Site Remediation | X04.1 Assess and Mitigate Site Hazards | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | X05. Enhanced Material Restrictions | X05.1 Select Compliant Interior Furnishings | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | X05.2 Select Compliant Architectural and Interior Products | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | X06. VOC Restrictions | X06.1 Limit VOCs from Wet-Applied Products | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  |  |  | X06.2 Restrict VOC Emissions from Furniture, Architectural and Interior Products | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | X07. Materials Transparency | X07.1 Select Products with Disclosed Ingredients | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | X07.2 Select Products with Enhanced Ingredient Disclosure | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | X07.3 Select Products with Third-Party Verified Ingredients | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | X08. Materials Optimization | X08.1 Select Materials with Enhanced Chemical Restrictions | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | X08.2 Select Optimized Products | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | X09. Waste Management | X09.1 Implement a Waste Management Plan | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | X10. Pest Management and Pesticide Use | X10.1 Manage Pests | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | X11. Cleaning Products and Protocols | X11.1 Improve Cleaning Practices | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | X11.2 Select Preferred Cleaning Products | 1 | Yes | 1 | Achieved | 1 |  | X12 Hidden | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | X12. β - Contact Reduction | X12.1 Reduce Respiratory Particle Exposure | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | X12.2 Address Surface Hand Touch | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 10 |  | 10 |  | 10 | 0 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | MIND | P | M01. Mental Health Promotion | M01.1 Promote Mental Health and Well-being | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | M02. Nature and Place | M02.1 Provide Connection to Nature | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | M02.2 Provide Connection to Place | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | M03. Mental Health Services | M03.1 Offer Mental Health Screening | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | M03.2 Offer Mental Health Services | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | M03.3 Offer Workplace Support | 1 | Yes | 1 | Achieved | 1 |  | M03.4 Hidden | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | M03.4 β Support Mental Health Recovery | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M04. Mental Health Education | M04.1 Offer Mental Health Education | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | M04.2 Offer Mental Health Education for Managers | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M05. Stress Management | M05.1 Develop Stress Management Plan | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M06. Restorative Opportunities | M06.1 Support Healthy Working Hours | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | M06.2 Provide Nap Policy and Space | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M07. Restorative Spaces | M07.1 Provide Restorative Spaces | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | M08. Restorative Programming | M08.1 Provide Restorative Programming | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M09. Enhanced Access to Nature | M09.1 Provide Nature Access Indoors | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | M09.2 Provide Nature Access Outdoors | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | M10. Tobacco Cessation | M10.1 Provide Tobacco Cessation Resources | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | M10.2 Limit Tobacco Availability | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | M11. Substance Use Services | M11.1 Offer Substance Use Education | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | M11.2 Provide Non-Workplace Sleep Support | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
[5 empty] | 7 |  | 7 |  | 7 | 0 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
P | COMMUNITY | P | C01. Health and Wellness Promotion | C01.1 Provide WELL Feature Guide | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | C02. Integrative Design | C02.1 Facilitate Stakeholder Charrette | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | C02.2 Promote Health-Oriented Mission | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | C03. Emergency Preparedness | C03.1 Develop Emergency Preparedness Plan | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  | P | C04. Occupant Survey | C04.1 Point Select Project Survey | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
P |  |  |  | C04.2 Administer Survey and Report Results | 0 | Required | Required | Achieved | Required | Required |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
O |  | O | C05. Enhanced Occupant Survey | C05.1 Utilize Enhanced Survey | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C05.2 Utilize Pre- and Post-Occupancy Survey | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C05.3 Implement Action Plan | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C05.4 Facilitate Interviews, Focus Groups and/or Observation | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C06. Health Services and Benefits | C06.1 Promote Health Benefits | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  |  |  | C06.2 Offer On-Demand Health Services | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C06.3 Offer Sick Leave | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C06.4 Support Community Immunity | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C07. Enhanced Health and Wellness Promotion | C07.1 Promote Culture of Health | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C07.2 Establish Health Promotion Leader | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C08. New Parent Support | C08.1 Offer New Parent Leave | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C09. New Mother Support | C09.1 Offer Workplace Breastfeeding Support | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C09.2 Design Lactation Room | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  | O | C10. Family Support | C10.1 Offer Childcare Support | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | C10.2 Offer Family Leave | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C10.3 Offer Bereavement Support | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C11. Civic Engagement | C11.1 Promote Civic Engagement | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C11.2 Provide Community Space | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C12. Organizational Transparency | C12.1 Promote Diversity and Inclusion | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | C13. Accessibility and Universal Design | C13.1 Integrate Universal Design | 2 | Yes | 2 | Achieved | 2 |  |  | FALSE | FALSE | FALSE | FALSE | 2 | 0 | 0
O |  | O | C14. Emergency Resources | C14.1 Promote Emergency Resources | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  |  |  | C14.2 Provide Opioid Response Kit and Training | 0 | No |  | Not Attempted |  |  | C15/C16/C17/C18 Hidden | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C15. β - Emergency Resilience and Recovery | C15.1 Promote Business Continuity | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C15.2 Support Emergency Resilience | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C15.3 Facilitate Healthy Re-entry | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C15.4 Establish Health Entry Requirements | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C16. β - Housing Equity | C16.1 Allocate Affordable Units | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C17. β - Responsible Labor Practices | C17.1 Disclose Labor Practices | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  |  |  | C17.2 Implement Responsible Labor Practices | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | C18. β - Support for Victims of Domestic Violence | C18.1 Support Victims of Domestic Violence | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 9 |  | 9 |  | 9 | 0 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[12 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O | INNOVATIONS | O | I01. Innovate WELL | I01.1 Propose Innovations |  | No |  | Not Attempted | [8 empty] | 0 | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
[5 empty] | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0
O |  | O | I02. WELL Accredited Professional (WELL AP) | I02.1 WELL AP | 1 | Yes | 1 | Achieved | 1 |  |  | FALSE | FALSE | FALSE | FALSE | 1 | 0 | 0
O |  | O | I03. Educate WELL | I03.1 Offer WELL Educational Tours | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
O |  | O | I04. Gateways to Wellness | I04.1 Complete Health and Wellness Program | 0 | No |  | Not Attempted |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
|  | O | I05. Green Building Rating Systems | I05.1 Achieve Sustainable Building Certification | 0 | No |  | Not Attempted
|  | O | I06. β - Carbon Disclosure and Reduction | I06.1 Carbon Inventory | 0 | 0
|  |  |  | I06.2 Carbon Reduction Goal | 0 | 0
|  |  |  | I06.3 Carbon Reduction | 0 | 0
O |  |  |  | I06.4 Carbon Neutral | 0 | 0 | [5 empty] | FALSE | FALSE | FALSE | FALSE | FALSE | 0 | 0
[5 empty] | 1 |  | 1 |  | 1 | 0

## Review Comments
Hide these columns before printing to PDF
2202025160 - Pohlad Office - Gateway22
Concept | Type | Feature | Part | Points Attempted | Pursuing | Status | Review Comment
General Project Observations:
This report reflects the results of the Performance Verification that occurred August 29th - September 1st, and September 13th, 2022. Comments have been recorded for all attempted Preconditions and Optimizations reflecting the results of the Performance Verification site visit. Refer to the individual part comments for specific details. Note for future Performance Testing submittals: I. Performance Verification Submittals cannot be provided via links to external sites as all data, photographs, and documentation must be loaded into WELL Online prior to submitting for review. II. Include a list of all equipment used along with device specifications and certificates of calibration showing the calibration date and calibration frequency requirements as per the Performance Verification Guidebook. III. Do not submit a project with known non-compliant preconditions. All known non-compliant preconditions must be corrected by the project team and retested prior to submittal and only compliant results submitted. IV. Do not submit a project with known non-compliant optimizations. All known non-compliant optimizations should either A) be corrected by the project team and retested prior to submittal or B) withdrawn by the project team. Ensure that only compliant results are submitted. | [8 empty] | Status and TA MISMATCH | PV and Status MISMATCH | Anticipated/PV MISMATCH | Not Attempted and Comment MISMATCH | TA Match | TA Status | PV Match | PV Status | Special Rule Flags
Air General Observations:
AIR | P | A01. Air Quality | A01.1 Meet Thresholds for Particulate Matter |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results have been provided, is unclear what calculations have been used for PM2.5 and PM10 as the raw data and calculation sheet do not appear to have been included. Include the raw data and a calculation spreadsheet showing the acclimation values, the median of at least 50 measurements, and calculation conversions for all testing results. Ensure to include an updated Performance Testing Submittal report with the final results. PRELIMINARY DOCUMENTATION REVIEW: Option 1. This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 779 | 0 | 736 | 0 | 0 | 0
|  |  | A01.2 Meet Thresholds for Organic Gases |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results from an ILAC accredited laboratory have been provided, it is unclear if the laboratory is accredited to test each individual contaminant. See the global published AAP #00093 for additional information (https://v2.wellcertified.com/en/v/air/feature/1). Either provide evidence that the laboratory is certified to test each contaminant or provide updated laboratory testing results from a compliant laboratory, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report to confirm compliance. Alternatively, provide documentation to adhere to AAP #00093 if a compliant laboratory is not available. 2. While field notes have been provided in the Air Field Notes tab, it appears the volume calculation used 1 liter flow rate at start and 0.3 liters at finish while the photographs show ~0.3 liters flow rate at start and end. As the start and end flow rates do not match the photographs and the Actual Volume does not match the values provided to the laboratory compliance cannot be confirmed. Provide an updated Performance Testing Submittal report that includes the corrected start and end flow rates, corrected ug/m3 based on the actual flow rates and ug per tube. Ensure to include all calculations and conversions. PRELIMINARY DOCUMENTATION REVIEW: Option 1. This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 1622 | 0 | 1579 | 0 | 0 | 0
|  |  | A01.3 Meet Thresholds for Inorganic Gases |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results have been provided, is unclear what calculations have been used for carbon monoxide and ozone as the raw data and calculation sheet do not appear to have been included. Include the raw data and a calculation spreadsheet showing the acclimation values, the median of at least 50 measurements, and calculation conversions for all testing results. Ensure to include an updated Performance Testing Submittal report with the final results. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 780 | 0 | 737 | 0 | 0 | 0
|  |  | A01.4 Meet Thresholds for Radon |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that the project does not have regularly occupied space at or below grade; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | A01.5 Monitor Air Parameters |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: No documentation is required at this time. Note the following. I. Ensure that air testing records will be provided through WELL Online annually. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | A02. Smoke-Free Environment | A02.1 Prohibit Indoor Smoking |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | A02.2 Prohibit Outdoor Smoking |  | Required | Achieved | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided and confirm compliance. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0
| P | A03. Ventilation Design | A03.1 Ensure Adequate Ventilation |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | A04. Construction Pollution Management | A04.1 Mitigate Construction Pollution |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | A05. Enhanced Air Quality | A05.1 Meet Enhanced Thresholds for Particulate Matter | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results have been provided, is unclear what calculations have been used for PM2.5 and PM10 as the raw data and calculation sheet do not appear to have been included. Include the raw data and a calculation spreadsheet showing the acclimation values, the median of at least 50 measurements, and calculation conversions for all testing results. Ensure to include an updated Performance Testing Submittal report with the final results. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 769 | 0 | 726 | 0 | 0 | 0
|  |  | A05.2 Meet Enhanced Thresholds for Organic Gases | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results from an ILAC accredited laboratory have been provided, it is unclear if the laboratory is accredited to test each individual contaminant. See the global published AAP #00093 for additional information (https://v2.wellcertified.com/en/v/air/feature/1). Either provide evidence that the laboratory is certified to test each contaminant or provide updated laboratory testing results from a compliant laboratory, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report to confirm compliance. Alternatively, provide documentation to adhere to AAP #00093 if a compliant laboratory is not available. 2. While field notes have been provided in the Air Field Notes tab, it appears the volume calculation used 1 liter flow rate at start and 0.3 liters at finish while the photographs show ~0.3 liters flow rate at start and end. As the start and end flow rates do not match the photographs and the Actual Volume does not match the values provided to the laboratory compliance cannot be confirmed. Provide an updated Performance Testing Submittal report that includes the corrected start and end flow rates, corrected ug/m3 based on the actual flow rates and ug per tube. Ensure to include all calculations and conversions. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 1612 | 0 | 1569 | 0 | 0 | 0
|  |  | A05.3 Meet Enhanced Thresholds for Inorganic Gases | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results have been provided, is unclear what calculations have been used for carbon monoxide and nitrogen dioxide as the raw data and calculation sheet do not appear to have been included. Include the raw data and a calculation spreadsheet showing the acclimation values, the median of at least 50 measurements, and calculation conversions for all testing results. Ensure to include an updated Performance Testing Submittal report with the final results. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 791 | 0 | 748 | 0 | 0 | 0
| O | A06. Enhanced Ventilation Design | A06.1 Increase Outdoor Air Supply |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | A06.2 Improve Ventilation Effectiveness |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A07. Operable Windows | A07.1 Provide Operable Windows |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | A07.2 Manage Window Use |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A08. Air Quality Monitoring and Awareness | A08.1 Install Indoor Air Monitors |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | A08.2 Promote Air Quality Awareness |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A09. Pollution Infiltration Management | A09.1 Design Healthy Entryways | 1 | Yes | Achieved | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided and confirm compliance. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0
|  |  | A09.2 Perform Envelope Commissioning |  | No | Withdrawn | FINAL DOCUMENTATION REVIEW: This part has been withdrawn. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While a narrative has been provided, the envelope commissioning plan and report are required to confirm compliance. Provide a technical document addressing each section of this part to demonstrate compliance with the requirements of this part. | [5 empty] | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | A10. Combustion Minimization | A10.1 Manage Combustion |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A11. Source Separation | A11.1 Manage Pollution and Exhaust |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A12. Air Filtration | A12.1 Implement Particle Filtration | 1 | Yes | Achieved | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided and confirm compliance. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. Note the following. I. Ensure that evidence of the filter replacement according to the manufacturer's recommendation is provided through WELL Online annually. | [5 empty] | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0
| O | A13. Enhanced Supply Air | A13.1 Improve Supply Air |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | A14. Microbe and Mold Control | A14.1 Implement Ultraviolet Air Treatment |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Water General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
WATER | P | W01. Water Quality Indicators | W01.1 Verify Water Quality Indicators |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results from an ILAC accredited laboratory have been provided, it is unclear if the laboratory is accredited to test each individual contaminant. See the global published AAP #00093 for additional information (https://v2.wellcertified.com/en/v/water/feature/2). Either provide evidence that the laboratory is certified to test each contaminant or provide updated laboratory testing results from a compliant laboratory, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report to confirm compliance. Alternatively, provide documentation to adhere to AAP #00093 if a compliant laboratory is not available. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 994 | 0 | 951 | 0 | 0 | 0
| P | W02. Drinking Water Quality | W02.1 Meet Chemical Thresholds |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results from an ILAC accredited laboratory have been provided, it is unclear if the laboratory is accredited to test each individual contaminant. See the global published AAP #00093 for additional information (https://v2.wellcertified.com/en/v/water/feature/2). Either provide evidence that the laboratory is certified to test each contaminant or provide updated laboratory testing results from a compliant laboratory, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report to confirm compliance. Alternatively, provide documentation to adhere to AAP #00093 if a compliant laboratory is not available. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 994 | 0 | 951 | 0 | 0 | 0
|  |  | W02.2 Meet Thresholds for Organics and Pesticides |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | W03. Basic Water Management | W03.1 Monitor Chemical and Biological Water Quality |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: No documentation is required at this time. Note the following. I. Ensure that water testing records will be provided through WELL Online annually. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | W03.2 Implement Legionella Management Plan |  | Required | Achieved | FINAL DOCUMENTATION REVIEW: Additional documentation has been provided. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While a governing guideline documentation has been provided outlining a Legionella Management Plan, it is unclear if project-specific roles, monitoring actions, critical control points, verification, and documentation are included. Provide an updated Legionella Management Plan to confirm compliance with the requirements of sections b1 and b3. 2. While documentation has been provided, it is unclear if a list of project-specific monitoring actions for relevant variables, list of critical control points, and verification and validation procedures are included. Provide an updated Legionella Management Plan that clarifies or includes additional information to confirm compliance with the requirements of sections b4, b5, and b6. | [5 empty] | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | W04. Enhanced Water Quality | W04.1 Meet Thresholds for Drinking Water Taste | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing results from an ILAC accredited laboratory have been provided, it is unclear if the laboratory is accredited to test each individual contaminant. See the global published AAP #00093 for additional information (https://v2.wellcertified.com/en/v/water/feature/2). Either provide evidence that the laboratory is certified to test each contaminant or provide updated laboratory testing results from a compliant laboratory, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report to confirm compliance. Alternatively, provide documentation to adhere to AAP #00093 if a compliant laboratory is not available. PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 994 | 0 | 951 | 0 | 0 | 0
| O | W05. Drinking Water Quality Management | W05.1 Assess and Maintain Drinking Water Quality |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | W05.2 Promote Drinking Water Transparency |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | W06. Drinking Water Promotion | W06.1 Ensure Drinking Water Access |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | W07. Moisture Management | W07.1 Design Envelope for Moisture Protection |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | W07.2 Design Interiors for Moisture Management |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | W07.3 Implement Mold and Moisture Management Plan | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Note the following. I. Ensure that the inspection results will be provided through WELL Online annually. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | W08. Hygiene Support | W08.1 Provide Bathroom Accommodations |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | W08.2 Enhance Bathroom Accommodations |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | W08.3 Support Effective Handwashing | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While photographs have been provided, it is unclear if the column of water is at least 3 inches from the rear of the sink. Provide additional photographs with measurements and the water running such that compliance can be confirmed for Part 3c3. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | W09 Hidden |  |  |  |  | 154 | 1 | 499 | 0 | 0 | 0 | 0 | 0
|  |  | W08.4 Provide Handwashing Supplies And Signage |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | W09 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | W09. β - Onsite Non-Potable Water Reuse | W09.1 Implement Safety Plan for Non-Potable Water Capture and Reuse | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Nourishment General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
NOURISHMENT | P | N01. Fruits and Vegetables | N01.1 Provide Fruits and Vegetables |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N01.2 Promote Fruit and Vegetable Visibility |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
| P | N02. Nutritional Transparency | N02.1 Provide Nutritional Information |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | N02.2 Address Food Allergens |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: This part is not applicable to the project type. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | N02.3 Label Sugar Content |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: This part is not applicable to the project type. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | N03. Refined Ingredients | N03.1 Limit Total Sugars |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | N03.2 Promote Whole Grains |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N04. Food Advertising | N04.1 Optimize Food Advertising |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N05. Artificial Ingredients | N05.1 Limit Artificial Ingredients |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N06. Portion Sizes | N06.1 Promote Healthy Portions |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N07. Nutrition Education | N07.1 Provide Nutrition Education |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N08. Mindful Eating | N08.1 Support Mindful Eating | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | N09. Special Diets | N09.1 Accommodate Special Diets |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | N09.2 Label Food Allergens |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N10. Food Preparation | N10.1 Provide Meal Support | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
| O | N11. Responsible Food Sourcing | N11.1 Implement Responsible Sourcing |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N12. Food Production | N12.1 Provide Gardening Space |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | N13. Local Food Environment | N13.1 Ensure Local Food Access | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | N14 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | N14. β - Red and Processed Meats | N14.1 Limit Red and Processed Meats | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Light General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
LIGHT | P | L01. Light Exposure | L01.1 Provide Indoor Light |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | L02. Visual Lighting Design | L02.1 Provide Visual Acuity |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing data has been provided, it appears the space types walking, reading, and eating that are listed in the Performance Testing Submittal report do not match the space types as provided by the project team during the documentation phase. Provide an updated Performance Testing Submittal report with the appropriate space types and targeted lux levels to confirm compliance. 2. While testing data has been provided, it appears the calibration certificate for the light sensor device has not been provided. Provide confirmation of the equipment calibration date and manufacturer specifications detailing how often calibration is required. FINAL DOCUMENTATION REVIEW: Additional documentation has been provided. PRELIMINARY DOCUMENTATION REVIEW: Option 1. Documentation has been provided. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While a photometric plan has been provided, it is unclear what the illuminance thresholds are for all tasks and activities within each space type. Provide design specifications which detail the illuminance thresholds in foot candles or lux for all tasks and activities for each space type (including transition areas, breakrooms, kitchen/pantry areas, etc.); as well as each accompanying height per space type to demonstrate compliance with the requirements for Part 1b. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 1614 | 0 | 0 | 0 | 0 | 0
| O | L03. Circadian Lighting Design | L03.1 Meet Lighting for Day-Active People |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | L04. Electric Light Glare Control | L04.1 Manage Glare from Electric Lighting |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | L05. Daylight Design Strategies | L05.1 Implement Daylight Plan |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | L05.2 Integrate Solar Shading | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
| O | L06. Daylight Simulation | L06.1 Conduct Daylight Simulation | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | L07. Visual Balance | L07.1 Balance Visual Lighting |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | L08. Electric Light Quality | L08.1 Enhance Color Rendering Quality |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | L08.2 Manage Flicker | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | L09. Occupant Lighting Control | L09.1 Enhance Occupant Controllability |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | L09.2 Provide Supplemental Lighting |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Movement General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
MOVEMENT | P | V01. Active Buildings and Communities | V01.1 Design Active Buildings and Communities |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: This part has no required documentation. Note the following. I. This feature is dependent on achieving at least one point under Feature V03: Circulation Network, Feature V04: Facilities for Active Occupants, Feature V05: Site Planning and Selection, or Feature V08: Physical Activity Spaces and Equipment. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0
| P | V02. Ergonomics Workstation Design | V02.1 Support Visual Ergonomics |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | V02.2 Provide Height-Adjustable Work Surfaces |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | V02.3 Provide Chair Adjustability |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | V02.4 Provide Support at Standing Workstations |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that employees are not regularly required to stand for 50% or more of their working hours; therefore, the precondition has been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | V02.5 Provide Workstation Orientation |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | V03. Circulation Network | V03.1 Design Aesthetic Staircases | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | V03.2 Integrate Point-of-Decision Signage |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | V03.3 Promote Visible Stairs | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | V04. Facilities for Active Occupants | V04.1 Provide Cycling Infrastructure | 2 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | V04.2 Provide Showers, Lockers and Changing Facilities | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | V05. Site Planning and Selection | V05.1 Select Sites with Pedestrian-friendly Streets |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | V05.2 Select Sites with Access to Mass Transit | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | V06. Physical Activity Opportunities | V06.1 Offer Physical Activity Opportunities |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | V07. Active Furnishings | V07.1 Provide Active Workstations | 2 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
| O | V08. Physical Activity Spaces and Equipment | V08.1 Provide Indoor Activity Spaces | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | V08.2 Provide Outdoor Physical Activity Space | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | V09. Physical Activity Promotion | V09.1 Offer Physical Activity Incentives |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | V10. Self-Monitoring | V10.1 Provide Self-Monitoring Tools |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | V11. β Ergonomics Programming | V11.1 Implement an Ergonomics Program | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | V11.2 Commit to Ergonomic Improvements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | V11.3 Support Remote Work Ergonomics | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Thermal Comfort General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
THERMAL COMFORT | P | T01. Thermal Performance | T01.1 Provide Acceptable Thermal Environment |  | Required | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While testing data has been provided, it appears that the metabolic rates and clothing values as provided by the project team have not been used. Provide an updated Performance Testing Submittal report with PPD and PMV values that utilize the metabolic rate and clothing values as provided in the narrative by the project team. PRELIMINARY DOCUMENTATION REVIEW: Option 1. Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 217 | 1 | 654 | 0 | 0 | 0 | 0 | 0
|  |  | T01.2 Monitor Thermal Parameters |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: No documentation is required at this time. Note the following. I. Ensure that thermal testing results are submitted through WELL Online annually. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | T02. Verified Thermal Performance | T02.1 Survey for Thermal Comfort |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | T03. Thermal Zoning | T03.1 Provide Thermostat Control |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | T04. Individual Thermal Control | T04.1 Provide Personal Cooling Options | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | T04.2 Provide Personal Heating Options | 1 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have not been provided. To demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. Provide geotagged and date/time-stamped photographs to demonstrate compliance with the requirements for this part. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 149 | 1 | 363 | 0 | 0 | 0 | 0 | 0
|  |  | T04.3 Allow Flexible Dress Code | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | T05. Radiant Thermal Comfort | T05.1 Implement Radiant Heating |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | T05.2 Implement Radiant Cooling |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | T06. Thermal Comfort Monitoring | T06.1 Monitor Thermal Environment |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | T07. Humidity Control | T07.1 Manage Relative Humidity |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | T09/T09 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | T08. β - Enhanced Operable Windows | T08.1 Provide Windows with Multiple Opening Modes | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | T09. β - Outdoor Thermal Comfort | T09.1 Manage Outdoor Heat | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | T09.2 Avoid Excessive Wind | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | T09.3 Support Outdoor Nature Access | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Sound General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
SOUND | P | S01. Sound Mapping | S01.1 Label Acoustic Zones |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | S01.2 Provide Acoustic Design Plan |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | S02. Maximum Noise Levels | S02.1 Limit Background Noise Levels |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | S03. Sound Barriers | S03.1 Design for Sound Isolation at Walls and Doors | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | S03.2 Achieve Sound Isolation at Walls | 2 | Yes | Pending Documentation | PRELIMINARY PERFORMANCE REVIEW: The on-site assessment results have been provided. See Appendix A for the performance testing data for this part. However, they do not confirm compliance because the Noise Isolation Class (NIC) testing results are below the minimum threshold required to achieve this part. COMMENTS TO BE ADDRESSED 1. Updated testing results, floor plans, photographs of equipment setup, field notes, and an updated Performance Testing Submittal report maybe provided during the Final Performance Review. PRELIMINARY DOCUMENTATION REVIEW: Option 1. This part has no required documentation. Requirements of this part will be verified through on-site assessment during your Performance Verification. | [5 empty] | 307 | 1 | 610 | 0 | 567 | 0 | 0 | 0
| O | S04. Reverberation Time | S04.1 Achieve Reverberation Time Thresholds |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | S05. Sound Reducing Surfaces | S05.1 Implement Sound Reducing Surfaces |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | S07/S08 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | S06. Minimum Background Sound | S06.1 Provide Minimum Background Sound |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | S06.2 Provide Enhanced Speech Reduction |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | S07. β - Impact Noise Management | S07.1 Specify Impact Noise Reducing Flooring | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | S07.2 Meet Thresholds for Impact Noise Rating | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | S08. β - Enhanced Audio Devices | S08.1 Provide Enhanced Speech Intelligibility | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | S08.2 Prioritize Audio Devices and Policies | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Materials General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
MATERIALS | P | X01. Material Restrictions | X01.1 Restrict Asbestos |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X01.2 Restrict Mercury |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X01.3 Restrict Lead |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | X02. Interior Hazardous Material Management | X02.1 Manage Asbestos Hazards |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that the building was built after asbestos was banned; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X02.2 Manage Lead Paint Hazards |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that the building was built after lead was banned; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X02.3 Manage Polychlorinated Biphenyl (PCB) Hazards |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that the building was built after Polychlorinated Biphenyl (PCB) was banned; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | X03. CCA and Lead Management | X03.1 Manage Exterior CCA Hazards |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that no outdoor structures have been built as a part of the current project scope; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X03.2 Manage Lead Hazards |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: The documentation indicates that wood structures and artificial turf are not part of the current project scope; therefore, the part requirements have been met. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X04. Site Remediation | X04.1 Assess and Mitigate Site Hazards |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | X05. Enhanced Material Restrictions | X05.1 Select Compliant Interior Furnishings |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | X05.2 Select Compliant Architectural and Interior Products | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X06. VOC Restrictions | X06.1 Limit VOCs from Wet-Applied Products | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X06.2 Restrict VOC Emissions from Furniture, Architectural and Interior Products | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X07. Materials Transparency | X07.1 Select Products with Disclosed Ingredients | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X07.2 Select Products with Enhanced Ingredient Disclosure | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X07.3 Select Products with Third-Party Verified Ingredients |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | X08. Materials Optimization | X08.1 Select Materials with Enhanced Chemical Restrictions |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | X08.2 Select Optimized Products |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | X09. Waste Management | X09.1 Implement a Waste Management Plan | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X10. Pest Management and Pesticide Use | X10.1 Manage Pests | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X11. Cleaning Products and Protocols | X11.1 Improve Cleaning Practices | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X11.2 Select Preferred Cleaning Products | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | X12 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | X12. β - Contact Reduction | X12.1 Reduce Respiratory Particle Exposure | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | X12.2 Address Surface Hand Touch | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Mind General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
MIND | P | M01. Mental Health Promotion | M01.1 Promote Mental Health and Well-being |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | M02. Nature and Place | M02.1 Provide Connection to Nature |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | M02.2 Provide Connection to Place |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | M03. Mental Health Services | M03.1 Offer Mental Health Screening | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | M03.2 Offer Mental Health Services | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | M03.3 Offer Workplace Support | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | M03.4 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | M03.4 β Support Mental Health Recovery |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M04. Mental Health Education | M04.1 Offer Mental Health Education | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | M04.2 Offer Mental Health Education for Managers |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M05. Stress Management | M05.1 Develop Stress Management Plan |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M06. Restorative Opportunities | M06.1 Support Healthy Working Hours |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | M06.2 Provide Nap Policy and Space |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M07. Restorative Spaces | M07.1 Provide Restorative Space | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | M08. Restorative Programming | M08.1 Provide Restorative Programming |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M09. Enhanced Access to Nature | M09.1 Provide Nature Access Indoors |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | M09.2 Provide Nature Access Outdoors | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | M10. Tobacco Cessation | M10.1 Provide Tobacco Cessation Resources |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | M10.2 Limit Tobacco Availability |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | M11. Substance Use Services | M11.1 Offer Substance Use Education |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | M11.2 Provide Substance Use and Addiction Services | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
| Community General Observations: | [15 empty] | 0 | 0 | 0 | 0
[17 empty] | 0 | 0 | 0 | 0
COMMUNITY | P | C01. Health and Wellness Promotion | C01.1 Provide WELL Feature Guide |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | C02. Integrative Design | C02.1 Facilitate Stakeholder Charrette |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C02.2 Promote Health-Oriented Mission |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | C03. Emergency Preparedness | C03.1 Develop Emergency Preparedness Plan |  | Required | Achieved | FINAL DOCUMENTATION REVIEW: Additional documentation has been provided. PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. However, to demonstrate compliance, the following must be addressed. COMMENTS TO BE ADDRESSED 1. While a policy has been provided, it implies an intent to comply with the part requirements instead of providing the project-specific Emergency Preparedness Plan (for example - this appears to be a template and there are blanks instructing someone to enter the project-specific information). Provide a project-specific Emergency Preparedness Plan addressing each section, with annotations if needed, that complies with the part requirements. | [5 empty] | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| P | C04. Occupant Survey | C04.1 Select Project Survey |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C04.2 Administer Survey and Report Results |  | Required | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. Note the following. I. Ensure that the survey results are submitted through WELL Online annually. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C05. Enhanced Occupant Survey | C05.1 Utilize Enhanced Survey |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C05.2 Utilize Pre- and Post-Occupancy Survey |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C05.3 Implement Action Plan |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C05.4 Facilitate Interviews, Focus Groups and/or Observation |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C06. Health Services and Benefits | C06.1 Promote Health Benefits | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C06.2 Offer On-Demand Health Services |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C06.3 Offer Sick Leave |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C06.4 Support Community Immunity |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C07. Enhanced Health and Wellness Promotion | C07.1 Promote Culture of Health |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C07.2 Establish Health Promotion Leader |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C08. New Parent Support | C08.1 Offer New Parent Leave |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C09. New Mother Support | C09.1 Offer Workplace Breastfeeding Support |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C09.2 Design Lactation Room | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C10. Family Support | C10.1 Offer Childcare Support | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C10.2 Offer Family Leave |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C10.3 Offer Bereavement Support |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C11. Civic Engagement | C11.1 Promote Community Engagement |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
|  |  | C11.2 Provide Community Space |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C12. Diversity and Inclusion | C12.1 Promote Diversity and Inclusion | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C13. Accessibility and Universal Design | C13.1 Integrate Universal Design | 2 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C14. Emergency Resources | C14.1 Promote Emergency Resources | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C14.2 Provide Opioid Response Kit and Training |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | C15/C16/C17 Hidden |  |  |  |  | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | C15. β - Emergency Resilience and Recovery | C15.1 Promote Business Continuity | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C15.2 Support Emergency Resilience | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C15.3 Facilitate Healthy Re-entry | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C15.4 Establish Health Entry Requirements | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C16. β - Housing Equity | C16.1 Allocate Affordable Units | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C17. β - Responsible Labor Practices | C17.1 Disclose Labor Practices | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | C17.2 Implement Responsible Labor Practices | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | C18. β - Support for Victims of Domestic Violence | C18.1 Support Victims of Domestic Violence | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Innovations General Observations:
INNOVATIONS | O | I01. Innovate WELL | I01.1 Propose Innovations | NA | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | When not attempted - use a Not Attempted status and put 'No' in column G with the standard not attempted review comment. There is no need to sum up the total I01 point in column F for cell F265. If any I01 Parts are attempted at any phase, the review comment in I265 should be "Refer to review comments for each proposed Innovation below." |  |  |  |  | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
[8 empty] | Use a separate row for each Innovation proposed under I01 and ensure to fill in the points and status for each. Hide rows that are not used. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | Ensure Innovation points are manually entered correctly. DO NOT 'copy/paste' from the downloaded scorecard as they will not align correctly in I01. |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | I02. WELL Accredited Professional (WELL AP) | I02.1 Achieve WELL AP | 1 | Yes | Achieved | PRELIMINARY DOCUMENTATION REVIEW: Documentation has been provided. | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| O | I03. Experience WELL Certification | I03.1 Offer WELL Educational Tours |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | I04. Gateways to Wellness | I04.1 Complete Health and Wellness Programs |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | I05. Green Building Rating Systems | I05.1 Achieve Green Building Certification |  | No | Not Attempted | PRELIMINARY DOCUMENTATION REVIEW: This part has not been attempted. | [5 empty] | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 1
| O | I06. β - Carbon Disclosure and Reduction | I06.1 Carbon Inventory | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | I06.2 Carbon Reduction Goal | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | I06.3 Carbon Reduction | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | I06.4 Carbon Neutral | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manually adjust points in column G, as needed to account for Feature level point caps If a change is made, highlight the cell red for visibility during QC

## Air
2202025160 - Pohlad Office - Gateway22 | [12 empty] | Hide Rows
Appendix A | [12 empty] | No | Put 1's in all rows for Parts that are not attempted. Do the formatting of the cell border before filtering on 0's.
August 29th - September 1st, and September 13th 2022 On-site Performance Verification Summary of Results | [12 empty] | No
No
| AIR | [11 empty] | No
|  | GENERAL OBSERVATIONS: There were no unusual conditions observed during the indoor air quality testing. | [10 empty] | No
|  | A01 Fundamental Air Quality - Part 1 | [10 empty] | No
|  |  | Location Name | PM2.5 (ug/m3) |  | PM10 (ug/m3) | Tolerance Applied | Outcome |  |  |  |  | No |  |  | Tolerances
|  | Measurement | WELL Building Standard threshold limit | 15 |  | 50 | 18/60 | (MET/NOT MET) |  |  |  |  | No |  |  | 18 | 60
|  | 1 | 5th floor café | TBD |  | TBD |  | TBD |  |  |  |  | No |  |  | PM2.5-OVER | PM10-OVER
|  | 2 | 5th floor office area | TBD |  | TBD |  | TBD |  |  |  |  | No |  |  | PM2.5-OVER | PM10-OVER
|  | 3 | 7th floor office area | TBD |  | TBD |  | TBD |  |  |  |  | No |  |  | PM2.5-OVER | PM10-OVER
|  | 4 | 6th floor reception | TBD |  | TBD |  | TBD |  |  |  |  | No |  |  | PM2.5-OVER | PM10-OVER
|  | 5 | 6th floor office area | TBD |  | TBD |  | TBD |  |  |  |  | No |  |  | PM2.5-OVER | PM10-OVER
|  | 6 | [10 empty] | Yes
|  | 7 | [10 empty] | Yes
|  | 8 | [10 empty] | Yes
|  | 9 | [10 empty] | Yes
|  | 10 | [10 empty] | Yes
|  | A01 Fundamental Air Quality - Part 2 | [10 empty] | No
|  |  | Location Name | Formaldehyde (ug/m3) 50-00-0 |  | Benzene (ug/m3) 71-43-2 | Toluene (ug/m3) 108-88-3 | VOC Tolerance Applied | Outcome |  |  |  | No
|  | Measurement | WELL Building Standard threshold limit | 50 | Tolerance Applied | 10 | 300 | 1 or more VOC's | MET/NOT MET |  |  |  | No |  |  | VOC Tolerance applied? | [8 empty] | Tolerance | Over Tolerance
|  | 1 | 5th floor café | TBD |  | TBD | TBD | No | TBD |  |  | High Flow | No | For the US EPA TO-17 method only |  | Over | Over | #VALUE! | #VALUE! |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
[8 empty] | No |  |  |  | Low Flow | Yes |  | Results from the high flow tube are reported unless there is suspicion of a breakthrough event, then the low flow tube is used. If a breakthrough event is suspected, documentation describing the reasoning for using the low flow must be included with the submittal. |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 2 | 5th floor office area | TBD |  | TBD | TBD | No | TBD |  |  | High Flow | No |  | Low flow results (if above detection limit) must be within 25% of the high flow results (if above detection limit) | Over | Over | #VALUE! | #VALUE! |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
[8 empty] | No |  |  |  | Low Flow | Yes |  | If either are below detection limit, just report the lab detection limit for either (or both) tubes. |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 3 | 7th floor office area | TBD |  | TBD | TBD | No | TBD |  |  | High Flow | No | FOR ALL OTHER METHODOLOGIES, report the values in the high flow rows and leave the low flow rows blank |  | Over | Over | #VALUE! | #VALUE! |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
[8 empty] | No |  |  |  | Low Flow | Yes | For all methodologies, ensure that the lab detection threshold is reported instead of ND |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 4 | 6th floor reception | TBD |  | TBD | TBD | No | TBD |  |  | High Flow | No | For all methodologies, ensure the field blank values are also recorded. |  | Over | Over | #VALUE! | #VALUE! |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 5 | 6th floor office area | TBD |  | TBD | TBD | No | TBD |  |  | High Flow | No |  |  | Over | Over | #VALUE! | #VALUE! |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 6 | [5 empty] | No |  |  |  | High Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 7 | [5 empty] | No |  |  |  | High Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 8 | [5 empty] | No |  |  |  | High Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 9 | [5 empty] | No |  |  |  | High Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | 10 | [5 empty] | No |  |  |  | High Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
[8 empty] | No |  |  |  | Low Flow | Yes |  |  |  |  | #VALUE! |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 0
|  | Field Blank | Field blank 1 | <0.1 |  | <2.58 | <3.05 |  |  |  |  | Add additional rows if needed | No |  |  | Over | Over |  |  |  | #REF! | #REF! | #REF! | #REF! | 0 | 2
|  | A01 Fundamental Air Quality - Part 3 | [10 empty] | No
|  |  | Location Name | Carbon Monoxide (ppm) |  | Ozone (ppb) | Tolerance Applied | Outcome |  |  |  |  | No
|  | Measurement | WELL Building Standard threshold limit | 9 |  | 51 | Ozone: 53.55 | (MET/NOT MET) |  |  |  |  | No |  |  | O3
|  | 1 | 5th floor café | 3.5 |  | TBD | No | TBD |  |  |  |  | No
|  | 2 | 5th floor office area | 4.36 |  | TBD | No | TBD |  |  |  |  | No
|  | 3 | 7th floor office area | 3.98 |  | TBD | No | TBD |  |  |  |  | No
|  | 4 | 6th floor reception | 4.09 |  | TBD | No | TBD |  |  |  |  | No
|  | 5 | 6th floor office area | 4.51 |  | TBD | No | TBD |  |  |  |  | No
|  | 6 | [10 empty] | Yes
|  | 7 | [10 empty] | Yes
|  | 8 | [10 empty] | Yes
|  | 9 | [10 empty] | Yes
|  | 10 | [10 empty] | Yes
|  | A05 Enhanced Air Quality - Part 1 | [10 empty] | No
|  |  | Location Name | PM2.5 (ug/m3) One/Two Points |  | PM10 (ug/m3) One/Two Points | Tolerance Applied | Tolerance Applied | Outcome | PM Threshold met |  |  | No |  |  | PM2.5 1 point | PM2.5 2 points | PM10 1 point | PM10 2 Points
|  | Measurement | WELL Building Standard threshold limit | 12/10 |  | 30/20 | PM2.5 (1 pt/2 pt) | PM10 (1 pt/2 pt) | (MET/NOT MET) | (one or two points) |  |  | No |  |  | 12 | 10 | 30 | 20 | Points
|  | 1 | 5th floor café | TBD |  | TBD | No/No | No/No | TBD | 1 |  |  | No | [6 empty] | 1
|  | 2 | 5th floor office area | TBD |  | TBD | No/No | No/No | TBD | 1 |  |  | No | [6 empty] | 1
|  | 3 | 7th floor office area | TBD |  | TBD | No/No | No/No | TBD | 1 |  |  | No | [6 empty] | 1
|  | 4 | 6th floor reception | TBD |  | TBD | No/No | No/No | TBD | 1 |  |  | No | [6 empty] | 1
|  | 5 | 6th floor office area | TBD |  | TBD | No/No | No/No | TBD | 1 |  |  | No | [6 empty] | 1
|  | 6 | [7 empty] | 1 |  |  | Yes
|  | 7 | [7 empty] | 1 |  |  | Yes
|  | 8 | [7 empty] | 1 |  |  | Yes
|  | 9 | [7 empty] | 1 |  |  | Yes
|  | 10 | [7 empty] | 1 |  |  | Yes
|  | A05 Enhanced Air Quality - Part 2 | [10 empty] | No
|  |  | Location Name | Acetaldehyde (ug/m3) 75-07-0 |  | Acrylonitrile (ug/m3) 107-13-1 | Benzene (ug/m3) 71-43-2 | Formaldehyde (ug/m3) 50-00-0 | Naphthalene (ug/m3) 91-20-3 | Toluene (ug/m3) 108-88-3 | Outcome |  | No
|  | Measurement | WELL Building Standard threshold limit | 140 (147) |  | 5 (5.25) | 3 (3.15) | 9 (10.8) | 9 (9.45) | 300 (315) | (MET / NOT MET) |  | No
|  | 1 | 5th floor café | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  | No
|  | 2 | 5th floor office area | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  | No
|  | 3 | 7th floor office area | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  | No
|  | 4 | 6th floor reception | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  | No
|  | 5 | 6th floor office area | TBD |  | TBD | TBD | TBD | TBD | TBD | TBD |  | No
|  | 6 | [10 empty] | Yes
|  | 7 | [10 empty] | Yes
|  | 8 | [10 empty] | Yes
|  | 9 | [10 empty] | Yes
|  | 10 | [10 empty] | Yes
|  | Field Blank | Field blank 1 | <0.1 |  | <1.75 | <2.58 | <0.1 | <4.23 | <3.05 |  |  | No
|  | A05 Enhanced Air Quality - Part 3 | [10 empty] | No
|  |  | Location Name | Carbon Monoxide (7 mg/m3 or 6 ppm) |  | Nitrogen dioxide (40 ug/m3 or 21 ppb) | Tolerance Applied | Outcome |  |  |  |  | No
|  | Measurement | WELL Building Standard threshold limit | 6 |  | 21 | N02: 25.2 | (MET/NOT MET) |  |  |  |  | No
|  | 1 | 5th floor café | 3.5 |  | TBD |  | TBD |  |  |  |  | No
|  | 2 | 5th floor office area | 4.36 |  | TBD |  | TBD |  |  |  |  | No
|  | 3 | 7th floor office area | 3.98 |  | TBD |  | TBD |  |  |  |  | No
|  | 4 | 6th floor reception | 4.09 |  | TBD |  | TBD |  |  |  |  | No
|  | 5 | 6th floor office area | 4.51 |  | TBD |  | TBD |  |  |  |  | No
|  | 6 | [10 empty] | Yes
|  | 7 | [10 empty] | Yes
|  | 8 | [10 empty] | Yes
|  | 9 | [10 empty] | Yes
|  | 10 | [10 empty] | Yes

## Water
2202025160 - Pohlad Office - Gateway22 | [11 empty] | Hide Rows
Appendix A | [11 empty] | No
August 29th - September 1st, and September 13th 2022 On-site Performance Verification Summary of Results | [11 empty] | No
No
| WATER | [10 empty] | No
|  | GENERAL OBSERVATIONS: No unusual conditions were observed on-site during the water sampling. The fifth floor restroom was tested twice to ensure accuracy. | [9 empty] | No
|  | W01 Water Quality Indicators | [9 empty] | No
|  |  | Location Name | Turbidity (NTU) | Total coliforms | Outcome | [5 empty] | No
|  | Measurement | WELL Building Standard threshold limit | 1 | Must Not Be Detected | (MET / NOT MET) | [5 empty] | No
|  | Configuration 1 Sample 1 | no filter - 5th floor restroom | 0.77667 | ND | TBD | [5 empty] | No
|  | Configuration 1 Sample 2 | no filter 6th floor restroom | 0.15667 | ND | TBD | [5 empty] | No
|  | Configuration 2 Sample 1 | soda stream 6th floor café | 0.37667 | ND | TBD | [5 empty] | No
|  | Configuration 3 Sample 1 | bottle filler 6th floor sink | 0.40333 | ND | TBD | [5 empty] | No
|  | Configuration 3 Sample 1 | [9 empty] | Yes
Yes
|  | W02 Drinking Water Quality Part 1 | [9 empty] | No
|  |  | Location Name | Arsenic (mg/L) | Cadmium (mg/L) | Chromium (mg/L) | Copper (mg/L) | Fluoride (mg/L) | Lead (mg/L) | Mercury (mg/L) | Nickel (mg/L) | No
|  | Measurement | WELL Building Standard threshold limit | 0.01 | 0.003 | 0.05 | 2 | 1.5 | 0.01 | 0.002 | 0.07 | No
|  | Configuration 2 Sample 1 | soda stream 6th floor café | <0.002 | <0.00015 | <0.002 | <0.002 | 0.68 | <0.0005 | <0.0001 | <0.002 | No
|  | Configuration 3 Sample 1 | bottle filler 6th floor sink | <0.002 | <0.00015 | <0.002 | 0.048 | 0.68 | <0.0005 | <0.0001 | <0.002 | No
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 2 | [9 empty] | Yes
|  | W02 Drinking Water Quality Part 1 (cont) | [9 empty] | No
|  |  | Location Name | Nitrate as N (mg/L) | Nitrite as N (mg/L) | Total Chlorine (mg/L) | Free Chlorine (mg/L) | Total Trihalomethanes (mg/L) | Total Haloacetic Acid (mg/L) | Outcome |  | No
|  | Measurement | WELL Building Standard threshold limit | 11 | 0.9 | 5 | < 4 | 0.08 | 0.06 | (MET/NOT MET) |  | No
|  | Configuration 2 Sample 1 | soda stream 6th floor café | 2.1 | 0.79 | 0.02 | 0.01 | 0.056 | 0.003 | TBD |  | No
|  | Configuration 3 Sample 1 | bottle filler 6th floor sink | 0.26 | 0.12 | 0.03 | 1.04 | 0.0277 | 0.0173 | TBD |  | No
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 2 | [9 empty] | Yes
|  | W02 Drinking Water Quality - Part 2 | [9 empty] | Yes
|  |  | Location Name | Atrazine (mg/L) | 2,4-dichlorophenoxyacetic Acid (mg/L) | Toluene (mg/L) | Xylenes (Total: m, p, and o) (mg/L) | Tetrachloroethylene (mg/L) | Outcome |  |  | Yes
|  | Measurement | WELL Building Standard threshold limit | 0.1 | 0.03 | 0.7 | 0.5 | 0.02 | (MET/NOT MET) |  |  | Yes
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 3 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 2 | [9 empty] | Yes
|  | W04 Enhanced Water Quality - Part 1 | [9 empty] | No
|  |  | Location Name | Aluminum (mg/L) | Chloride (mg/L) | Copper (mg/L) | Manganese (mg/L) | Iron (mg/L) | Silver (mg/L) | Sodium (mg/L) | Sulfates (mg/L) | No
|  | Measurement | WELL Building Standard threshold limit | 0.2 | 250 | 1 | 0.05 | 0.3 | 0.1 | 270 | 250 | No
|  | Configuration 2 Sample 1 | soda stream 6th floor café | 0.09 | 23.9 | <0.002 | <0.001 | 0.22 | 0.0001 | 16.8 | 22.7 | No
|  | Configuration 3 Sample 1 | bottle filler 6th floor sink | <0.05 | 23.1 | 0.048 | 0.001 | 0.22 | 0.00011 | 16.2 | 22.8 | No
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 2 | [9 empty] | Yes
|  | W04 Enhanced Water Quality - Part 1 (cont) | [9 empty] | No
|  |  | Location Name | Sulfide (mg/L) | Zinc (mg/L) | Total Dissolved Solids (mg/L) | Free Chlorine (mg/L) | Outcome |  |  |  | No
|  | Measurement | WELL Building Standard threshold limit | 0.05 | 5 | 500 | 1.25 | (MET/NOT MET) |  |  |  | No
|  | Configuration 2 Sample 1 | soda stream 6th floor café | 1 | <0.01 | 150 | 0.01 | TBD |  |  |  | No
|  | Configuration 3 Sample 1 | bottle filler 6th floor sink | <0.5 | <0.01 | 152 | 1.04 | TBD |  |  |  | No
|  | Configuration 2 Sample 1 | [9 empty] | Yes
|  | Configuration 2 Sample 2 | [9 empty] | Yes

## Light
2202025160 - Pohlad Office - Gateway22 | [10 empty] | Hide Rows
Appendix A | [10 empty] | No
August 29th - September 1st, and September 13th 2022 On-site Performance Verification Summary of Results | [10 empty] | No
No
| LIGHT | [9 empty] | No
|  | GENERAL OBSERVATIONS: Task lighting was turned on at work areas that had it built into an overhead cabinet (enclosed office) or at workstations were a task light was located. Sunset at 7:52pm. | [8 empty] | No | Submittal Notes
|  | L02 Visual Lighting Design - Part 1 | [8 empty] | No | Only update cells in GREEN
|  |  | Requirement | Task/Space Use Type | Target Illuminance (lux) | Average Illuminance per Task/Space Use (lux) | Minimum Illuminance per Task/Space Use (lux) | At least 3 samples per Task/Space Use | Outcome (MET/NOT MET) | Notes | No | Space types are determined by the Project Team and should match the lighting standard space types
|  | Part 1a | Ambient lighting maintains average target level for each task type AND The lowest light level of each target type is at least half of the target level | Walking | 100 | 249.3333 | 124 | Yes - 3 | TBD |  | No | Do not insert above this row, or delete this row, formulas will become offset.
|  |  |  | Reading | 150 | 705.8409 | 107 | Yes - 44 | TBD |  | No | Insert rows for more task/space types
|  |  |  | Eating | 100 | 256.3333 | 197 | Yes - 3 | TBD |  | No | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Insert rows for more task/space types
[11 empty] | Yes | Do not insert below this row, or delete this row, formulas will become offset. Use this row as your last space use type and hide the blank rows above
|  | Detailed Measurement Data | [8 empty] | No
|  | Measurement Point | Work Plane / Location / Description | Task/Space Type (use drop down only) | Illuminance Result (lux) | Half target (lux) | Illuminance is at least half the target level (MET/NOT MET) | Average Illuminance per Space Use (lux) | Location Outcome (MET/NOT MET) | Notes | No | Target Illuminance Values are established by the project team. See documentation under L02
|  | 1 | Reception/Lobby | Reading | 331 | 75 | MET | 705.8409 | MET |  | No | Task and space types are determined by the Project Team and will be pulled from the task/space types entered in E8-E19*
|  | 2 | Reception/Lobby | Reading | 328 | 75 | MET | 705.8409 | MET |  | No
|  | 3 | Reception/Lobby | Reading | 147 | 75 | MET | 705.8409 | NOT MET |  | No
|  | 4 | Enclosed Office | Reading | 757 | 75 | MET | 705.8409 | MET |  | No
|  | 5 | Enclosed Office | Reading | 783 | 75 | MET | 705.8409 | MET |  | No | Note that a Location Outcome can be NOT MET but project still pass as long as the value is > 1/2 the value and the average of the task/space type > target
|  | 6 | Enclosed Office | Reading | 706 | 75 | MET | 705.8409 | MET |  | No
|  | 7 | Open Office | Reading | 158 | 75 | MET | 705.8409 | MET |  | No
|  | 8 | Enclosed Office | Reading | 597 | 75 | MET | 705.8409 | MET |  | No
|  | 9 | Enclosed Office | Reading | 210 | 75 | MET | 705.8409 | MET |  | No
|  | 10 | Corridor | Walking | 124 | 50 | MET | 249.3333 | MET |  | No
|  | 11 | Conference Room | Reading | 681 | 75 | MET | 705.8409 | MET |  | No
|  | 12 | Open Office | Reading | 107 | 75 | MET | 705.8409 | NOT MET |  | No
|  | 13 | Open Office | Reading | 708 | 75 | MET | 705.8409 | MET |  | No
|  | 14 | Corridor | Reading | 389 | 75 | MET | 705.8409 | MET |  | No
|  | 15 | Open Office | Reading | 1525 | 75 | MET | 705.8409 | MET |  | No
|  | 16 | Enclosed Office | Reading | 550 | 75 | MET | 705.8409 | MET |  | No
|  | 17 | Enclosed Office | Reading | 407 | 75 | MET | 705.8409 | MET |  | No
|  | 18 | Conference Room | Reading | 772 | 75 | MET | 705.8409 | MET |  | No
|  | 19 | Conference Room | Reading | 947 | 75 | MET | 705.8409 | MET |  | No
|  | 20 | Enclosed Office | Reading | 578 | 75 | MET | 705.8409 | MET |  | No
|  | 21 | Enclosed Office | Reading | 507 | 75 | MET | 705.8409 | MET |  | No
|  | 22 | café | Eating | 241 | 50 | MET | 256.3333 | MET |  | No
|  | 23 | café | Eating | 331 | 50 | MET | 256.3333 | MET |  | No
|  | 24 | café | Eating | 197 | 50 | MET | 256.3333 | MET |  | No
|  | 25 | Corridor | Walking | 383 | 50 | MET | 249.3333 | MET |  | No
|  | 26 | Enclosed Office | Reading | 599 | 75 | MET | 705.8409 | MET |  | No
|  | 27 | Enclosed Office | Reading | 602 | 75 | MET | 705.8409 | MET |  | No
|  | 28 | Enclosed Office | Reading | 658 | 75 | MET | 705.8409 | MET |  | No
|  | 29 | Open Office | Reading | 2006 | 75 | MET | 705.8409 | MET |  | No
|  | 30 | Open Office | Reading | 2000 | 75 | MET | 705.8409 | MET |  | No
|  | 31 | Enclosed Office | Reading | 611 | 75 | MET | 705.8409 | MET |  | No
|  | 32 | Enclosed Office | Reading | 497 | 75 | MET | 705.8409 | MET |  | No
|  | 33 | Enclosed Office | Reading | 373 | 75 | MET | 705.8409 | MET |  | No
|  | 34 | Enclosed Office | Reading | 561 | 75 | MET | 705.8409 | MET |  | No
|  | 35 | Open Office | Reading | 1380 | 75 | MET | 705.8409 | MET |  | No
|  | 36 | Enclosed Office | Reading | 529 | 75 | MET | 705.8409 | MET |  | No
|  | 37 | Enclosed Office | Reading | 709 | 75 | MET | 705.8409 | MET |  | No
|  | 38 | copy room | Reading | 3099 | 75 | MET | 705.8409 | MET |  | No
|  | 39 | Corridor | Walking | 241 | 50 | MET | 249.3333 | MET |  | No
|  | 40 | Enclosed Office | Reading | 349 | 75 | MET | 705.8409 | MET |  | No
|  | 41 | Open Office | Reading | 253 | 75 | MET | 705.8409 | MET |  | No
|  | 42 | Open Office | Reading | 2106 | 75 | MET | 705.8409 | MET |  | No
|  | 43 | Enclosed Office | Reading | 309 | 75 | MET | 705.8409 | MET |  | No
|  | 44 | Enclosed Office | Reading | 454 | 75 | MET | 705.8409 | MET |  | No
|  | 45 | Conference Room | Reading | 655 | 75 | MET | 705.8409 | MET |  | No
|  | 46 | Enclosed Office | Reading | 493 | 75 | MET | 705.8409 | MET |  | No
|  | 47 | Conference Room | Reading | 718 | 75 | MET | 705.8409 | MET |  | No
|  | 48 | lounge | Reading | 219 | 75 | MET | 705.8409 | MET |  | No
|  | 49 | Conference Room | Reading | 315 | 75 | MET | 705.8409 | MET |  | No
|  | 50 | Conference Room | Reading | 374 | 75 | MET | 705.8409 | MET |  | No | Unhide additional cells for rows 51-100
No
|  | L03 Circadian Lighting Design - Part 1 | [8 empty] | Yes
|  |  |  | Performance Verification Results (EML) | Points Achieved in L05 | Half Target Outcome (MET/NOT MET) | Points Achieved |  | Overall Outcome (MET/NOT MET) | Tolerance Applied | Yes | [7 empty] | EML + Tolerance
|  | #NUM! |  | #NUM! | 0 | #NUM! | #NUM! |  | #NUM! | #NUM! | Yes | [7 empty] | #NUM!
|  | Detailed Measurement Data | [8 empty] | Yes | Note that all testing for v2 is performed after dark. The options for daylighting require achievement of L05 and no daytime testing is required. |  | Threshold | Met | L05 Points |  | Half Threshold | W/tolerance
|  | Measurement Point | Location / Description | Nighttime Testing Results (EML) | EML with Tolerance Applied | Half Threshold (EML) | Notes |  |  |  | Yes |  | EL 1 point | 150 |  | 0 |  | #NUM! |  | 1 | Electric light only 150 EML | 150 EML (1 point)
|  | 1 | [8 empty] | Yes |  | EL 3 Points | 240 |  | 0 |  |  |  | 3 | Electric light only 240 EML | 240 EML (3 points)
|  | 2 | [8 empty] | Yes |  | EL + L05 1 Point | 120 |  | 0 |  |  |  | 1 | Electric light and daylighting 120 EML with electric lighting and at least 2 points in Feature L05: Enhanced Daylight Access | 120 EML with electric lighting and at least 2 points in Feature L05: Enhanced Daylight Access
|  | 3 | [8 empty] | Yes |  | EL + L05 3 Points | 180 |  | 0 | Sum |  |  | 3 | Electric light and daylighting 180 EML with electric lighting and at least 2 points in Feature L05: Enhanced Daylight Access | 180 EML with electric lighting and at least 2 points in Feature L05: Enhanced Daylight Access
|  | 4 | [8 empty] | Yes
|  | 5 | [8 empty] | Yes
|  | 6 | [8 empty] | Yes
|  | 7 | [8 empty] | Yes
|  | 8 | [8 empty] | Yes
|  | 9 | [8 empty] | Yes
|  | 10 | [8 empty] | Yes
|  | 11 | [8 empty] | Yes
|  | 12 | [8 empty] | Yes
|  | 13 | [8 empty] | Yes
|  | 14 | [8 empty] | Yes
|  | 15 | [8 empty] | Yes
|  | 16 | [8 empty] | Yes
|  | 17 | [8 empty] | Yes
|  | 18 | [8 empty] | Yes
|  | 19 | [8 empty] | Yes
|  | 20 | [8 empty] | Yes
|  | 21 | [8 empty] | Yes
|  | 22 | [8 empty] | Yes
|  | 23 | [8 empty] | Yes
|  | 24 | [8 empty] | Yes
|  | 25 | [8 empty] | Yes
|  | 26 | [8 empty] | Yes
|  | 27 | [8 empty] | Yes
|  | 28 | [8 empty] | Yes
|  | 29 | [8 empty] | Yes
|  | 30 | [8 empty] | Yes
|  | 31 | [8 empty] | Yes
|  | 32 | [8 empty] | Yes
|  | 33 | [8 empty] | Yes
|  | 34 | [8 empty] | Yes
|  | 35 | [8 empty] | Yes
|  | 36 | [8 empty] | Yes
|  | 37 | [8 empty] | Yes
|  | 38 | [8 empty] | Yes
|  | 39 | [8 empty] | Yes
|  | 40 | [8 empty] | Yes
|  | 41 | [8 empty] | Yes
Yes
|  | XXX | Space with no working plane - 0 degrees | Ambient Light | [7 empty] | For projects with spaces without working planes that require measurement, use the formatting to the left. Note that the calculations above will need to be manually adjusted. See the PV Guidebook for further instructions on the measurement methodology.
|  | XXX | Space with no working plane - 90 degrees | Ambient Light
|  | XXX | Space with no working plane - 180 degrees | Ambient Light
|  | XXX | Space with no working plane - 270 degrees | Ambient Light
|  |  |  | Median | #NUM!

## Thermal Comfort
2202025160 - Pohlad Office - Gateway22 | [16 empty] | Hide Rows
Appendix A | [16 empty] | No
August 29th - September 1st, and September 13th 2022 On-site Performance Verification Summary of Results | [16 empty] | No
No
| THERMAL COMFORT | [15 empty] | No
|  | GENERAL OBSERVATIONS: No unusual conditions were noted during on-site testing. HVAC was on. | [14 empty] | No
|  | T01: Thermal Performance - Part 1 | [14 empty] | No |  |  |  | T7 Tolerance Calcs
|  | Measurement | Location / Description | Metabolic Rate | Clothing Value | Seated or Standing | Dry Bulb Temperature 1 (low/4") | Dry Bulb Temperature 2 (mid/ 24" or 43") | Dry Bulb Temperature 3 (high/ 43" or 67") | Dry Bulb Outcome (Median of Dry Bulb 1, 2, 3) | Mean Radiant Temperature (calculated) | Relative Humidity |  | PMV | PPD | Outcome T01.1 (MET/NOT MET) | No |  | Target L | Target H | MinLow | MaxHigh
[12 empty] | % | Tolerance Applied |  |  |  | No |  | 30 | 60 | 29.1 | 61.8
|  | 1 | 5th floor L1 | 1.1 | 0.5 | Standing | 73.7 | 72.67 | 72.93 | 72.93 | 70.7 | 51.17 | No | -0.48 | 10% | TBD | No | Replace with real data.
|  | 2 | 5th floor L2 | 1.1 | 0.5 | Standing | 72.87 | 72.86 | 72.52 | 72.86 | 71.1 | 50.44 | No | -0.46 | 9% | TBD | No | Ensure units of temp are consistent across all values, either Celsius or Fahrenheit
|  | 3 | 7th floor L3 | 1.1 | 0.5 | Seated | 74.11 | 73.97 | 74 | 74 | 75.1 | 50.99 | No | -0.42 | 9% | TBD | No | Mean Radiant Temperature(MRT) should be the calculated MRT
|  | 4 | 6th floor L4 | 1.1 | 0.5 | Standing | 71.56 | 72.82 | 72.74 | 72.74 | 72.4 | 48.28 | No | -0.41 | 8% | TBD | No
|  | 5 | 6th floor L5 | 1.1 | 0.5 | Seated | 72.49 | 73.62 | 73.45 | 73.45 | 72 | 45.89 | No | -0.57 | 12% | TBD | No
|  | 6 | 5th Floor L6 | 1.1 | 0.5 | Seated | 71.11 | 71.31 | 71.22 | 71.22 | 70.7 | 50.03 | No | -0.63 | 13% | TBD | No
|  | 7 | 5th Floor L7 | 1.1 | 0.5 | Seated | 71.41 | 71.98 | 71.92 | 71.92 | 72 | 49.06 | No | -0.49 | 10% | TBD | No
|  | 8 | 7th floor L8 | 1.1 | 0.5 | Seated | 73.18 | 72.63 | 72.54 | 72.63 | 73.5 | 50 | No | -0.34 | 7% | TBD | No
|  | 9 | 7th floor L9 | 1.1 | 0.5 | Seated | 73.36 | 74.03 | 73.84 | 73.84 | 74.8 | 49.58 | No | -0.15 | 5% | TBD | No
|  | 10 | 5th floor L10 | 1.1 | 0.5 | Seated | 69.9 | 70.42 | 70.32 | 70.32 | 69.2 | 53.79 | No | -0.6 | 12% | TBD | No
|  | 11 | 6th floor L11 | 1.1 | 0.5 | Seated | 71.81 | 72.03 | 72.05 | 72.03 | 73.2 | 52.32 | No | -0.39 | 8% | TBD | No
|  | 12 | 6th floor L12 | 1.1 | 0.5 | Seated | 72.59 | 75.71 | 72.92 | 72.92 | 73.3 | 46.95 | No | -0.34 | 7% | TBD | No
|  | 13 | 6th floor L13 | 1.1 | 0.5 | Seated | 73.71 | 74.93 | 74.09 | 74.09 | 73.3 | 47.26 | No | -0.23 | 6% | TBD | No
|  | 14 | 7th floor L14 | 1.1 | 0.5 | Seated | 72.6 | 74.22 | 74.33 | 74.22 | 72.7 | 50.32 | No | -0.24 | 6% | TBD | No
Yes
Yes
Yes
Yes
Yes
Yes
Yes
Yes

## Sound
2202025160 - Pohlad Office - Gateway22 | [10 empty] | Hide Rows
Appendix A | [10 empty] | No
August 29th - September 1st, and September 13th 2022 On-site Performance Verification Summary of Results | [10 empty] | No
No
| SOUND | [9 empty] | No
|  | GENERAL OBSERVATIONS: No unseal situations. HVAC was on. | [8 empty] | No
|  | S02 Background Noise | [8 empty] | Yes | For S02 Open offices, the reported value should be the average across each floor.
|  | Measurement Number | Location Name | Space Category | Measurement Type | WELL Building Standard Maximum Threshold (dB) Points Achieved | Test Result | Tolerance Applied | Outcome (MET/NOT MET) | Notes | Yes | Space types need to be selected from the drop down list as these are the only valid space types, see WELL the Addenda for more details
[5 empty] | Leq dBA | (3 Points) 35 dBA |  |  |  |  | Yes
[5 empty] | Leq dBC | (3 Points) 55 dBC |  |  |  |  | Yes
[5 empty] | Lmax dBA | (3 Points) 45 dBA |  |  |  |  | Yes
[5 empty] | Lmax dBC | (3 Points) 65 dBC |  |  |  |  | Yes
[5 empty] | Leq dBA | (3 Points) 40 dBA |  |  |  |  | Yes
[5 empty] | Leq dBC | (3 Points) 60 dBC |  |  |  |  | Yes
[5 empty] | Lmax dBA | (3 Points) 50 dBA |  |  |  |  | Yes
[5 empty] | Lmax dBC | (3 Points) 70 dBC |  |  |  |  | Yes
[5 empty] | Leq dBA | (3 Points) 45 dBA |  |  |  |  | Yes
[5 empty] | Leq dBC | (3 Points) 65 dBC |  |  |  |  | Yes
[5 empty] | Lmax dBA | (3 Points) 55 dBA |  |  |  |  | Yes
[5 empty] | Lmax dBC | (3 Points) 75 dBC |  |  |  |  | Yes | Do not delete rows to the left, just hide them before PDF'ing
[5 empty] | Leq dBA | (3 Points) 40 dBA |  |  |  |  | Yes
[5 empty] | Leq dBC | (3 Points) 60 dBC |  |  |  |  | Yes
[5 empty] | Lmax dBA | (3 Points) 50 dBA |  |  |  |  | Yes
[5 empty] | Lmax dBC | (3 Points) 70 dBC |  |  |  |  | Yes
[5 empty] | Leq dBA | (3 Points) 45 dBA |  |  |  |  | Yes | To add locations copy all 4 rows and insert above or below another set
[5 empty] | Leq dBC | (3 Points) 65 dBC |  |  |  |  | Yes
[5 empty] | Lmax dBA | (3 Points) 55 dBA |  |  |  |  | Yes
[5 empty] | Lmax dBC | (3 Points) 75 dBC |  |  |  |  | Yes
[5 empty] | Leq dBA | [5 empty] | Yes
[5 empty] | Leq dBC | [5 empty] | Yes
[5 empty] | Lmax dBA | [5 empty] | Yes
[5 empty] | Lmax dBC | [5 empty] | Yes
[5 empty] | Leq dBA | [5 empty] | Yes
[5 empty] | Leq dBC | [5 empty] | Yes
[5 empty] | Lmax dBA | [5 empty] | Yes
[5 empty] | Lmax dBC | [5 empty] | Yes
[5 empty] | Leq dBA | [5 empty] | Yes
[5 empty] | Leq dBC | [5 empty] | Yes | Do not delete rows to the left, just hide them before PDF'ing
[5 empty] | Lmax dBA | [5 empty] | Yes
[5 empty] | Lmax dBC | [5 empty] | Yes
|  | S03 Sound Barriers - Part 2 | [8 empty] | No
|  | Measurement | Receiving Room | Source Room | Measurement Type | WELL Building Standard Minimum Threshold (NIC) | Test Result (NIC) | Outcome (MET/NOT MET) |  | Notes | No
|  | 1 | Conference room | Lounge | Sound Pressure Level | 50 | 33 | TBD |  |  | No
|  | 2 | Conference room | Enclosed Office | Sound Pressure Level | 45 | 37 | TBD |  |  | No
|  | 3 | Enclosed Office | Enclosed Office | Sound Pressure Level | 45 | 39 | TBD |  |  | No
|  | 4 | Enclosed Office | open office area | Sound Pressure Level | 45 | 37 | TBD |  |  | No
|  | 5 | Conference room | Lounge | Sound Pressure Level | 50 | 30 | TBD |  |  | No
|  | 6 | Treadmill Office | Lounge | Sound Pressure Level | 50 | 28 | TBD |  |  | No
|  | 7 | Wellness Room | Corridor | Sound Pressure Level | 35 | 28 | TBD |  |  | No
|  | 8 | Enclosed Office | Corridor | Sound Pressure Level | 35 | 42 | MET |  |  | No
|  | 9 | Enclosed Office | Enclosed Office | Sound Pressure Level | 45 | 44 | TBD |  |  | No
|  | 10 | Enclosed Office | open office area | Sound Pressure Level | 45 | 30 | TBD |  |  | No
|  | 11 | Enclosed Office | Enclosed Office | Sound Pressure Level | 45 | 33 | TBD |  |  | No
|  | 12 | Open Collaboration | Conference Room | Sound Pressure Level | 50 | 32 | TBD |  |  | No
|  | 13 | Enclosed Office | Enclosed Office | Sound Pressure Level | 45 | 33 | TBD |  |  | No
|  | 14 | Enclosed Office | Phone Room | Sound Pressure Level | 45 | 33 | TBD |  |  | No
|  | 15 | Phone Room | Phone Room | Sound Pressure Level | 45 | 36 | TBD |  |  | No
|  | S04 Sound Absorption - Part 1 | [8 empty] | Yes
|  | Measurement | Location / Description | Measurement Type | WELL Building Standard Maximum Threshold (seconds) | Test Result (seconds) | Outcome (MET/NOT MET) | Notes |  |  | Yes
|  | 1 |  | Reverberation | [6 empty] | Yes
|  | 2 |  | Reverberation | [6 empty] | Yes
|  | 3 |  | Reverberation | [6 empty] | Yes
|  | 4 |  | Reverberation | [6 empty] | Yes
|  | S05 Sound Masking | [8 empty] | Yes
|  | Measurement | Location / Description | Measurement Type | WELL Building Standard Minimum Threshold (dB) | WELL Building Standard Maximum Threshold (dB) | Test Result (dB) | Outcome (MET/NOT MET) | Notes |  | Yes
|  | 1 |  | Sound Pressure (LAeq) | [6 empty] | Yes
|  | 2 |  | Sound Pressure (LAeq) | [6 empty] | Yes
|  | 3 |  | Sound Pressure (LAeq) | [6 empty] | Yes
|  | 4 |  | Sound Pressure (LAeq) | [6 empty] | Yes
|  | 5 |  | Sound Pressure (LAeq) | [6 empty] | Yes

## Lists (hidden)
Status | Review Phase | Anticipated Status | Not Anticipated Status | Pending Status | The values to the left drive the headers for the Overview tab. No need to sort, if sorted, include all columns in the sort | Pending Status Counts | Anticipated Status | Not Anticipated/Not Achieved Status | Pending Status Column | Pending On-Site Counts | REVIEW PHASE | VALID STATUS | Sort Order | List of valid status options | Data Validation List |  |  | <no longer used?
Achieved | Appeal Review | Achieved | Not Achieved |  |  | Pending | Achieved | Not Achieved | Pending | Pending On-site Assessment | Appeal Review | Achieved | 1 |  | Achieved | The values in Data Validation list are pulled from the List of Valid Status Options, that are driven off the combinations in REVIEW PHASE and VALID STATUS. To change the sort, it has to be changed ONLY in the VALID STATUS columns. To add a VALID STATUS to a REVIEW PHASE, or remove. Delete the text, or add the new combination at the bottom then reset column L and M. Do not Insert or Delete cells/rows in the Lists Tab | ID | Points attempted | Part
Anticipated | Curative Action Plan Review | Achieved | Not Achieved |  |  | Pending Documentation | Anticipated | Not Anticipated | Pending Documentation | Anticipated, Pending On-site Assessment | Appeal Review | Not Achieved | 2 |  | Pending Documentation |  | A01.1 | Required | Meet Thresholds for Particulate Matter
Anticipated, Pending On-site Assessment | Final Documentation Review | Anticipated | Not Anticipated | Pending |  |  |  |  | Pending Documentation, Pending On-site Assessment |  | Appeal Review | Withdrawn | 3 |  | Withdrawn |  | A01.2 | Required | Meet Thresholds for Organic Gases
Not Achieved | Final Performance Review | Achieved | Not Achieved | [5 empty] | Pending On-site Assessment |  | Appeal Review | Not Applicable | 4 |  | Withdrawn |  | A01.3 | Required | Meet Thresholds for Inorganic Gases
Not Anticipated | Final Precertification Review | Anticipated | Not Anticipated | Pending |  | Pending Doc/On-site Counts |  |  | Anticipated, Pending On-site Assessment |  | Appeal Review | Not Attempted | 5 |  | Not Attempted |  | A01.4 | Required | Meet Thresholds for Radon
Not Applicable | Final WELL Report | Achieved | Not Achieved |  |  | Pending Documentation, Pending On-site Assessment |  |  |  |  | Curative Action Plan Review | Achieved | 1 |  | Not Applicable |  | A01.5 | Required | Monitor Air Parameters
Not Attempted | Preliminary Documentation Review | Anticipated |  | Pending | [6 empty] | Curative Action Plan Review | Not Achieved | 2 |  | Not Achieved |  | A02.1 | Required | Prohibit Indoor Smoking
Partially Anticipated | Preliminary Performance Review | Achieved | Not Achieved | Pending | [6 empty] | Curative Action Plan Review | Withdrawn | 3 |  |  |  | A02.2 | Required | Prohibit Outdoor Smoking
Partially Achieved | Preliminary Recertification Documentation Review | Anticipated |  | Pending | [6 empty] | Curative Action Plan Review | Not Applicable | 4 |  |  |  | A03.1 | Required | Ensure Adequate Ventilation
Pending | Final Recertification Documentation Review | Anticipated | Not Anticipated | Pending |  |  | The values above drive the counts in the overview tab for review phases for the anticipated/achieved sums | The values above drive the counts for not anticipated/achieved sums on the overview | The values above drive the counts for pending sums on the overview tab |  | Curative Action Plan Review | Not Attempted | 5 |  |  |  | A04.1 | Required | Mitigate Construction Pollution
Pending Documentation | Preliminary Recertification Performance Review | Achieved | Not Anticipated | Pending | [6 empty] | Final Documentation Review | Anticipated | 1 |  |  | To Resort the status's by phase, update the numbering within each Phase, and then resort by Review Phase, then Sort Order. This will automatically resort in the drop down in the Comments Tab. | A05.1 | 1 point | Meet Enhanced Thresholds for Particulate Matter
Pending Documentation, Pending On-site Assessment | Final Recertification Performance Review | Achieved | Not Achieved | [7 empty] | Final Documentation Review | Anticipated, Pending On-site Assessment | 2 |  |  |  | A05.2 | 1 point | Meet Enhanced Thresholds for Organic Gases
Pending On-site Assessment | Preliminary Precertification Review | Anticipated |  | Pending | [6 empty] | Final Documentation Review | Not Anticipated | 3 |  |  |  | A05.3 | 1 point | Meet Enhanced Thresholds for Inorganic Gases
Withdrawn | [10 empty] | Final Documentation Review | Withdrawn | 4 |  |  |  | A06.1 | 1 point | Increase Outdoor Air Supply
The list above is no longer referenced, but is left here to indicate all possible status's that can be used in a report | [10 empty] | Final Documentation Review | Pending Documentation | 5 |  |  |  | A06.2 | 1 point | Improve Ventilation Effectiveness
[11 empty] | Final Documentation Review | Pending Documentation, Pending On-site Assessment | 6 |  |  |  | A07.1 | 1 point | Provide Operable Windows
[11 empty] | Final Documentation Review | Pending On-site Assessment | 7 |  |  |  | A07.2 | 1 point | Manage Window Use
[11 empty] | Final Performance Review | Achieved | 1 |  |  |  | A08.1 | 1 point | Install Indoor Air Monitors
[11 empty] | Final Performance Review | Not Achieved | 2 |  |  |  | A08.2 | 1 point | Promote Air Quality Awareness
[11 empty] | Final Performance Review | Withdrawn | 3 |  |  |  | A09.1 | 1 point | Design Healthy Entryways
[11 empty] | Final Performance Review | Not Applicable | 4 |  |  |  | A09.2 | 1 point | Perform Envelope Commissioning
Review Phase | The list to the left drives the review phase drop down on the Overview tab. The order here determines drop down order | [9 empty] | Final Performance Review | Not Attempted | 5 |  |  |  | A10.1 | 1 point | Manage Combustion
Preliminary Documentation Review | [10 empty] | Final Precertification Review | Anticipated | 1 |  |  | Explanation of Column P Formula: For each row in Column P, the formula uses the ROW() function to keep track of where it is at against the INDEX() that returns the value based on that location. Example: The data set O1:O99 is what is passed to the INDEX(), and only non blanks are returned to it. ROW(2:2) tells the INDEX to return row 2 from it’s data set (the 2nd row that is passed to the INDEX() without blanks). Note: Row 1 in the O1:O99 array is “List of valid status options”, Row 2 would be “Anticipated” for a prelim doc since all the blanks are now gone. | A11.1 | 1 point | Manage Pollution and Exhaust
Final Documentation Review | [10 empty] | Final Precertification Review | Not Attempted | 2 |  |  |  | A12.1 | 1 point | Implement Particle Filtration
Preliminary Precertification Review | [10 empty] | Final Precertification Review | Withdrawn | 3 |  |  |  | A13.1 | 1 point | Improve Supply Air
Final Precertification Review | [10 empty] | Final Precertification Review | Not Applicable | 4 |  |  |  | A14.1 | 1 point | Implement Ultraviolet Air Treatment
Preliminary Performance Review | [10 empty] | Final WELL Report | Achieved | 1 |  |  |  | W01.1 | Required | Verify Water Quality Indicators
Final Performance Review | [10 empty] | Final WELL Report | Not Achieved | 2 |  |  |  | W02.1 | Required | Meet Chemical Thresholds
Curative Action Plan Review | [10 empty] | Final WELL Report | Withdrawn | 3 |  |  |  | W02.2 | Required | Meet Thresholds for Organics and Pesticides
Appeal Review | [10 empty] | Final WELL Report | Not Attempted | 4 |  |  |  | W03.1 | Required | Monitor Chemical and Biological Water Quality
Final WELL Report | [10 empty] | Final WELL Report | Not Applicable | 5 |  |  |  | W03.2 | Required | Implement Legionella Management Plan
Preliminary Recertification Documentation Review | [10 empty] | Preliminary Documentation Review | Anticipated | 1 |  |  |  | W04.1 | 2 points | Meet Thresholds for Drinking Water Taste
Final Recertification Documentation Review | [10 empty] | Preliminary Documentation Review | Anticipated, Pending On-site Assessment | 2 |  |  |  | W05.1 | 2 points | Assess and Maintain Drinking Water Quality
Preliminary Recertification Performance Review | [10 empty] | Preliminary Documentation Review | Pending Documentation | 3 |  |  |  | W05.2 | 1 point | Promote Drinking Water Transparency
Final Recertification Performance Review | [10 empty] | Preliminary Documentation Review | Pending Documentation, Pending On-site Assessment | 4 |  |  |  | W06.1 | 1 point | Ensure Drinking Water Access
[11 empty] | Preliminary Documentation Review | Pending On-site Assessment | 5 |  |  |  | W07.1 | 1 point | Design Envelope for Moisture Protection
[11 empty] | Preliminary Documentation Review | Not Attempted | 6 |  |  |  | W07.2 | 1 point | Design Interiors for Moisture Management
Innovation I01.1 Special Data validation | I01.1 has special rules and thus status list | [9 empty] | Preliminary Documentation Review | Not Applicable | 7 |  |  |  | W07.3 | 1 point | Implement Mold and Moisture Management Plan
Achieved | [10 empty] | Preliminary Performance Review | Achieved | 1 | Achieved |  |  | W08.1 | 2 points | Provide Bathroom Accommodations
Anticipated | [10 empty] | Preliminary Performance Review | Pending Documentation | 2 | Pending Documentation |  |  | W08.2 | 1 point | Enhance Bathroom Accommodations
Anticipated, Pending On-site Assessment | [10 empty] | Preliminary Performance Review | Withdrawn | 3 | Withdrawn |  |  | W08.3 | 1 point | Support Effective Handwashing
Anticipated, Pending On-site Assessment | [10 empty] | Preliminary Performance Review | Withdrawn | 3 | Withdrawn |  |  | W08.4 | 1 point | Provide Handwashing Supplies And Signage
Not Achieved | [10 empty] | Preliminary Performance Review | Not Attempted | 4 | Not Attempted |  |  | W09.1 | 2 points | Implement Safety Plan for Non-Potable Water Capture and Reuse
Not Anticipated | [10 empty] | Preliminary Performance Review | Not Applicable | 5 | Not Applicable |  |  | N01.1 | Required | Provide Fruits and Vegetables
Not Applicable | [10 empty] | Preliminary Performance Review | Not Achieved | 6 | Not Achieved |  |  | N01.2 | Required | Promote Fruit and Vegetable Visibility
Not Attempted | [10 empty] | Preliminary Precertification Review | Anticipated | 1 |  |  |  | N02.1 | Required | Provide Nutritional Information
Partially Anticipated | [10 empty] | Preliminary Precertification Review | Pending Documentation | 2 |  |  |  | N02.2 | Required | Address Food Allergens
Partially Achieved | [10 empty] | Preliminary Precertification Review | Not Attempted | 3 |  |  |  | N02.3 | Required | Label Sugar Content
Pending | [10 empty] | Preliminary Precertification Review | Not Applicable | 4 |  |  |  | N03.1 | 1 point | Limit Total Sugars
Pending Documentation | [10 empty] | Final Precertification Review | Not Anticipated | 5 |  |  |  | N03.2 | 1 point | Promote Whole Grains
Pending Documentation, Pending On-site Assessment | [10 empty] | Final Recertification Performance Review | Achieved | 1 |  |  |  | N04.1 | 1 point | Optimize Food Advertising
Pending On-site Assessment | [10 empty] | Final Recertification Performance Review | Not Achieved | 2 |  |  |  | N05.1 | 1 point | Limit Artificial Ingredients
Withdrawn | [10 empty] | Final Recertification Performance Review | Withdrawn | 3 |  |  |  | N06.1 | 1 point | Promote Healthy Portions
[11 empty] | Final Recertification Performance Review | Not Applicable | 4 |  |  |  | N07.1 | 1 point | Provide Nutrition Education
[11 empty] | Final Recertification Performance Review | Not Attempted | 5 |  |  |  | N08.1 | 2 points | Support Mindful Eating
[11 empty] | Preliminary Recertification Performance Review | Achieved | 1 |  |  |  | N09.1 | 1 point | Accommodate Special Diets
[11 empty] | Preliminary Recertification Performance Review | Pending Documentation | 2 |  |  |  | N09.2 | 1 point | Label Food Allergens
[11 empty] | Preliminary Recertification Performance Review | Withdrawn | 3 |  |  |  | N10.1 | 1 point | Provide Meal Support
[11 empty] | Preliminary Recertification Performance Review | Not Anticipated | 4 |  |  |  | N11.1 | 1 point | Implement Responsible Sourcing
[11 empty] | Preliminary Recertification Performance Review | Not Attempted | 5 |  |  |  | N12.1 | 2 points | Provide Gardening Space
[11 empty] | Preliminary Recertification Performance Review | Not Applicable | 6 |  |  |  | N13.1 | 2 points | Ensure Local Food Access
[11 empty] | Preliminary Recertification Performance Review | Not Achieved | 7 |  |  |  | N14.1 | 1 point | Limit Red and Processed Meats
[11 empty] | Preliminary Recertification Documentation Review | Anticipated | 1 |  |  |  | L01.1 | Required | Provide Indoor Light
[11 empty] | Preliminary Recertification Documentation Review | Anticipated, Pending On-site Assessment | 2 |  |  |  | L02.1 | Required | Provide Visual Acuity
[11 empty] | Preliminary Recertification Documentation Review | Pending Documentation | 3 |  |  |  | L03.1 | 3 points | Meet Lighting for Day-Active People
[11 empty] | Preliminary Recertification Documentation Review | Pending Documentation, Pending On-site Assessment | 4 |  |  |  | L04.1 | 1 point | Manage Glare from Electric Lighting
[11 empty] | Preliminary Recertification Documentation Review | Pending On-site Assessment | 5 |  |  |  | L05.1 | 3 points | Implement Daylight Plan
[11 empty] | Preliminary Recertification Documentation Review | Not Attempted | 6 |  |  |  | L05.2 | 3 points | Integrate Solar Shading
[11 empty] | Preliminary Recertification Documentation Review | Not Applicable | 7 |  |  |  | L06.1 | 2 points | Conduct Daylight Simulation
[11 empty] | Final Recertification Documentation Review | Anticipated | 1 |  |  |  | L07.1 | 1 point | Balance Visual Lighting
[11 empty] | Final Recertification Documentation Review | Anticipated, Pending On-site Assessment | 2 |  |  |  | L08.1 | 1 point | Enhance Color Rendering Quality
[11 empty] | Final Recertification Documentation Review | Not Anticipated | 3 |  |  |  | L08.2 | 2 points | Manage Flicker
[11 empty] | Final Recertification Documentation Review | Withdrawn | 4 |  |  |  | L09.1 | 2 points | Enhance Occupant Controllability
[11 empty] | Final Recertification Documentation Review | Pending Documentation | 5 |  |  |  | L09.2 | 1 point | Provide Supplemental Lighting
[11 empty] | Final Recertification Documentation Review | Pending Documentation, Pending On-site Assessment | 6 |  |  |  | V01.1 | Required | Design Active Buildings and Communities
[11 empty] | Final Recertification Documentation Review | Pending On-site Assessment | 7 |  |  |  | V02.1 | Required | Support Visual Ergonomics
[17 empty] | V02.2 | Required | Provide Height-Adjustable Work Surfaces
[17 empty] | V02.3 | Required | Provide Chair Adjustability
[17 empty] | V02.4 | Required | Provide Support at Standing Workstations
[17 empty] | V02.5 | Required | Provide Workstation Orientation
[17 empty] | V03.1 | 1 point | Design Aesthetic Staircases
[17 empty] | V03.2 | 1 point | Integrate Point-of-Decision Signage
[17 empty] | V03.3 | 1 point | Promote Visible Stairs
[17 empty] | V04.1 | 2 points | Provide Cycling Infrastructure
[17 empty] | V04.2 | 1 point | Provide Showers, Lockers and Changing Facilities
[17 empty] | V05.1 | 2 points | Select Sites with Pedestrian-friendly Streets
[17 empty] | V05.2 | 2 points | Select Sites with Access to Mass Transit
[17 empty] | V06.1 | 2 points | Offer Physical Activity Opportunities
[17 empty] | V07.1 | 2 points | Provide Active Workstations
[17 empty] | V08.1 | 1 point | Provide Indoor Activity Spaces
[17 empty] | V08.2 | 1 point | Provide Outdoor Physical Activity Space
[17 empty] | V09.1 | 1 point | Offer Physical Activity Incentives
[17 empty] | V10.1 | 1 point | Provide Self-Monitoring Tools
[17 empty] | V11.1 | 1 point | Implement an Ergonomics Program
[17 empty] | V11.2 | 1 point | Commit to Ergonomic Improvements
[17 empty] | V11.3 | 1 point | Support Remote Work Ergonomics
[17 empty] | T01.1 | Required | Provide Acceptable Thermal Environment
[17 empty] | T01.2 | Required | Monitor Thermal Parameters
[17 empty] | T02.1 | 3 points | Survey for Thermal Comfort
[17 empty] | T03.1 | 2 points | Provide Thermostat Control
[17 empty] | T04.1 | 1 point | Provide Personal Cooling Options
[17 empty] | T04.2 | 1 point | Provide Personal Heating Options
[17 empty] | T04.3 | 1 point | Allow Flexible Dress Code
[17 empty] | T05.1 | 1 point | Implement Radiant Heating
[17 empty] | T05.2 | 1 point | Implement Radiant Cooling
[17 empty] | T06.1 | 1 point | Monitor Thermal Environment
[17 empty] | T07.1 | 1 point | Manage Relative Humidity
[17 empty] | T08.1 | 1 point | Provide Windows with Multiple Opening Modes
[17 empty] | T09.1 | 1 point | Manage Outdoor Heat
[17 empty] | T09.2 | 1 point | Avoid Excessive Wind
[17 empty] | T09.3 | 1 point | Support Outdoor Nature Access
[17 empty] | S01.1 | Required | Label Acoustic Zones
[17 empty] | S01.2 | Required | Provide Acoustic Design Plan
[17 empty] | S02.1 | 3 points | Limit Background Noise Levels
[17 empty] | S03.1 | 1 point | Design for Sound Isolation at Walls and Doors
[17 empty] | S03.2 | 1 point | Achieve Sound Isolation at Walls
[17 empty] | S04.1 | 2 points | Achieve Reverberation Time Thresholds
[17 empty] | S05.1 | 2 points | Implement Sound Reducing Surfaces
[17 empty] | S06.1 | 1 point | Provide Minimum Background Sound
[17 empty] | S06.2 | 1 point | Provide Enhanced Speech Reduction
[17 empty] | S07.1 | 1 point | Specify Impact Noise Reducing Flooring
[17 empty] | S07.2 | 2 points | Meet Thresholds for Impact Noise Rating
[17 empty] | S08.1 | 1 point | Provide Enhanced Speech Intelligibility
[17 empty] | S08.2 | 1 point | Prioritize Audio Devices and Policies
[17 empty] | X01.1 | Required | Restrict Asbestos
[17 empty] | X01.2 | Required | Restrict Mercury
[17 empty] | X01.3 | Required | Restrict Lead
[17 empty] | X02.1 | Required | Manage Asbestos Hazards
[17 empty] | X02.2 | Required | Manage Lead Paint Hazards
[17 empty] | X02.3 | Required | Manage Polychlorinated Biphenyl (PCB) Hazards
[17 empty] | X03.1 | Required | Manage Exterior CCA Hazards
[17 empty] | X03.2 | Required | Manage Lead Hazards
[17 empty] | X04.1 | 1 point | Assess and Mitigate Site Hazards
[17 empty] | X05.1 | 1 point | Select Compliant Interior Furnishings
[17 empty] | X05.2 | 1 point | Select Compliant Architectural and Interior Products
[17 empty] | X06.1 | 2 points | Limit VOCs from Wet-Applied Products
[17 empty] | X06.2 | 2 points | Restrict VOC Emissions from Furniture, Architectural and Interior Products
[17 empty] | X07.1 | 1 point | Select Products with Disclosed Ingredients
[17 empty] | X07.2 | 1 point | Select Products with Enhanced Ingredient Disclosure
[17 empty] | X07.3 | 1 point | Select Products with Third-Party Verified Ingredients
[17 empty] | X08.1 | 1 point | Select Materials with Enhanced Chemical Restrictions
[17 empty] | X08.2 | 1 point | Select Optimized Products
[17 empty] | X09.1 | 1 point | Implement a Waste Management Plan
[17 empty] | X10.1 | 1 point | Manage Pests
[17 empty] | X11.1 | 1 point | Improve Cleaning Practices
[17 empty] | X11.2 | 1 point | Select Preferred Cleaning Products
[17 empty] | X12.1 | 1 point | Reduce Respiratory Particle Exposure
[17 empty] | X12.2 | 1 point | Address Surface Hand Touch
[17 empty] | M01.1 | Required | Promote Mental Health and Well-being
[17 empty] | M02.1 | Required | Provide Connection to Nature
[17 empty] | M02.2 | Required | Provide Connection to Place
[17 empty] | M03.1 | 1 point | Offer Mental Health Screening
[17 empty] | M03.2 | 1 point | Offer Mental Health Services
[17 empty] | M03.3 | 1 point | Offer Workplace Support
[17 empty] | M03.4 | 1 point | β Support Mental Health Recovery
[17 empty] | M04.1 | 1 point | Offer Mental Health Education
[17 empty] | M04.2 | 1 point | Offer Mental Health Education for Managers
[17 empty] | M05.1 | 2 points | Develop Stress Management Plan
[17 empty] | M06.1 | 1 point | Support Healthy Working Hours
[17 empty] | M06.2 | 1 point | Provide Nap Policy and Space
[17 empty] | M07.1 | 1 point | Provide Restorative Space
[17 empty] | M08.1 | 1 point | Provide Restorative Programming
[17 empty] | M09.1 | 1 point | Provide Nature Access Indoors
[17 empty] | M09.2 | 1 point | Provide Nature Access Outdoors
[17 empty] | M10.1 | 2 points | Provide Tobacco Cessation Resources
[17 empty] | M10.2 | 1 point | Limit Tobacco Availability
[17 empty] | M11.1 | 1 point | Offer Substance Use Education
[17 empty] | M11.2 | 1 point | Provide Substance Use and Addiction Services
[17 empty] | C01.1 | Required | Provide WELL Feature Guide
[17 empty] | C02.1 | Required | Facilitate Stakeholder Charrette
[17 empty] | C02.2 | Required | Promote Health-Oriented Mission
[17 empty] | C03.1 | Required | Develop Emergency Preparedness Plan
[17 empty] | C04.1 | Required | Select Project Survey
[17 empty] | C04.2 | Required | Administer Survey and Report Results
[17 empty] | C05.1 | 1 point | Utilize Enhanced Survey
[17 empty] | C05.2 | 1 point | Utilize Pre- and Post-Occupancy Survey
[17 empty] | C05.3 | 1 point | Implement Action Plan
[17 empty] | C05.4 | 1 point | Facilitate Interviews, Focus Groups and/or Observation
[17 empty] | C06.1 | 2 points | Promote Health Benefits
[17 empty] | C06.2 | 1 point | Offer On-Demand Health Services
[17 empty] | C06.3 | 1 point | Offer Sick Leave
[17 empty] | C06.4 | 1 point | Support Community Immunity
[17 empty] | C07.1 | 1 point | Promote Culture of Health
[17 empty] | C07.2 | 1 point | Establish Health Promotion Leader
[17 empty] | C08.1 | 3 points | Offer New Parent Leave
[17 empty] | C09.1 | 1 point | Offer Workplace Breastfeeding Support
[17 empty] | C09.2 | 2 points | Design Lactation Room
[17 empty] | C10.1 | 1 point | Offer Childcare Support
[17 empty] | C10.2 | 1 point | Offer Family Leave
[17 empty] | C10.3 | 1 point | Offer Bereavement Support
[17 empty] | C11.1 | 1 point | Promote Community Engagement
[17 empty] | C11.2 | 1 point | Provide Community Space
[17 empty] | C12.1 | 1 point | Promote Diversity and Inclusion
[17 empty] | C13.1 | 2 points | Integrate Universal Design
[17 empty] | C14.1 | 1 point | Promote Emergency Resources
[17 empty] | C14.2 | 1 point | Provide Opioid Response Kit and Training
[17 empty] | C15.1 | 1 point | Promote Business Continuity
[17 empty] | C15.2 | 1 point | Support Emergency Resilience
[17 empty] | C15.3 | 1 point | Facilitate Healthy Re-entry
[17 empty] | C15.4 | 1 point | Establish Health Entry Requirements
[17 empty] | C16.1 | 2 points | Allocate Affordable Units
[17 empty] | C17.1 | 1 point | Disclose Labor Practices
[17 empty] | C17.2 | 2 points | Implement Responsible Labor Practices
[17 empty] | C18.1 | 2 points | Support Victims of Domestic Violence
[17 empty] | I01.1 | 10 points | Propose Innovations
[17 empty] | I02.1 | 1 point | Achieve WELL AP
[17 empty] | I03.1 | 1 point | Offer WELL Educational Tours
[17 empty] | I04.1 | 1 point | Complete Health and Wellness Programs
[17 empty] | I05.1 | 5 points | Achieve Green Building Certification